## Wind Turbines
ID # | SAM Entry Name | Model Name | SAM kW Rating | Nameplate Capacity (kW) | Rated Capacity at 11 m/s (kW) | SAM Rotor Diameter (m) | Corrected Rotor Diameter (m) | Commercially available as of February 2020? (Yes/No) | Certified to AWEA or IEC standards? (Yes/No/Past) | Date of Certification (Future Expiration Date or Last Known Date) | Power Curve Source | Duplicate? | Notes | SAM IEC Wind Speed Class | SAM original Wind Speed Array (m/s) | SAM original Power Curve Array (kW)
1 | Ampair 600-230 1.7m | Ampair 600-230 | 0.27 |  |  | 1 | 1.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.004¦0.035¦0.072¦0.113¦0.151¦0.184¦0.21¦0.23¦0.244¦0.246¦0.246¦0.251¦0.256¦0.26¦0.268¦0.27¦0.27¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
2 | Samrey Samprey Wren_1m_0.3kw | Samrey Wren 1m 0.3 kW | 0.28 |  |  | 1 | 1 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.005¦0.016¦0.032¦0.055¦0.08¦0.11¦0.135¦0.16¦0.18¦0.2¦0.22¦0.24¦0.25¦0.265¦0.27¦0.28¦0.28¦0.28¦0.28¦0.28¦0.28¦0.28¦0¦0¦0¦0¦0
3 | Energy Ball HEA V100 1.1m 0.6kW | Energy Ball V100 | 0.5 |  |  | 1 | 1.1 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.004¦0.011¦0.02¦0.036¦0.055¦0.079¦0.11¦0.15¦0.2¦0.25¦0.31¦0.38¦0.47¦0.5¦0.5¦0.5¦0.5¦0.5¦0.5¦0¦0¦0¦0¦0¦0¦0¦0
4 | Earth-Tech ET500_2.5m_500w | Earth-Tech ET500 | 0.698 |  |  | 2 | 2.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.026¦0.07¦0.114¦0.187¦0.337¦0.504¦0.61¦0.678¦0.698¦0.687¦0.66¦0.63¦0.594¦0.537¦0.447¦0.383¦0.32¦0.255¦0.19¦0.127¦0.063¦0¦0¦0¦0¦0¦0¦0
5 | Future Energy FE1012U 1.8m 1kW | FE1012U | 0.7 |  |  | 1 | 1.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.05¦0.1¦0.17¦0.24¦0.31¦0.36¦0.42¦0.49¦0.57¦0.63¦0.662¦0.7¦0.7¦0.7¦0.7¦0.7¦0.7¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
6 | Marlec FM1803-2 1.8m | FM1803-2 | 0.72 |  |  | 1 | 1.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.02¦0.04¦0.07¦0.11¦0.16¦0.23¦0.29¦0.36¦0.45¦0.53¦0.63¦0.72¦0.71¦0.6¦0.35¦0.27¦0.24¦0.25¦0.26¦0.27¦0.29¦0.3¦0.31¦0.33¦0.34¦0.35¦0.36
7 | Ampair 600-230 1.7m 0.7kw | Ampair 600-230 | 0.732 |  |  | 1 | 1.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.034¦0.07¦0.137¦0.252¦0.39¦0.524¦0.621¦0.699¦0.73¦0.732¦0.73¦0.73¦0.73¦0.73¦0.73¦0.73¦0.73¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
8 | Kestrel e230 2.3m 0.8kw | e230i | 0.815 |  |  | 2 | 2.3 | Yes | No | N/A |  |  | Available, but no known recent sales in USA | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.02¦0.048¦0.095¦0.16¦0.25¦0.38¦0.5¦0.6¦0.69¦0.78¦0.812¦0.815¦0.815¦0.815¦0.815¦0.815¦0.815¦0.815¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
9 | Tempower Whisper H40 2.1m 0.8kw | Whisper H40 | 0.914 |  |  | 2 | 2.1 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.019¦0.055¦0.107¦0.179¦0.264¦0.371¦0.49¦0.621¦0.767¦0.886¦0.914¦0.907¦0.886¦0.855¦0.819¦0.776¦0.738¦0.7¦0.662¦0.624¦0.586¦0.548¦0.51¦0.472¦0.434¦0.398¦0.36
10 | Hummer 2.7m 0.5kw | Hummer 2.7m 0.5 | 0.989 |  |  | 2 | 2.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.08¦0.17¦0.3¦0.46¦0.576¦0.682¦0.76¦0.82¦0.88¦0.93¦0.989¦0.989¦0.9¦0.81¦0.72¦0.645¦0.612¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
11 | Bergey BWC XL.1 | BWC XL.1 | 1 |  |  | 2.5 | 2.5 | No | No | N/A |  | 11, 15 | DELETE | 0 | 0¦3¦3.6¦5.4¦7.2¦8.9¦10.7¦12.5¦14.3¦16.1¦17.9¦19.7¦21¦23¦40 | 0¦0¦0.048¦0.155¦0.39¦0.69¦1.02¦1.22¦1.19¦1.085¦1.0¦0.9¦0.5¦0¦0
12 | Samrey Samprey Mistral_2m_1.15kw | Samrey Mistral 2m | 1.05 |  |  | 2 | 2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.04¦0.08¦0.14¦0.22¦0.31¦0.42¦0.53¦0.66¦0.75¦0.83¦0.9¦0.94¦0.98¦1.03¦1.05¦1.05¦1.05¦1.05¦1.05¦1.05¦1.05¦1.05¦0¦0¦0¦0¦0
13 | Kestrel 300i 3m 1kW | e300i | 1.1 |  |  | 3 | 3 | Yes | No | N/A |  |  | Available, but no known recent sales in USA | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.016¦0.08¦0.17¦0.299¦0.46¦0.63¦0.8¦0.95¦1.07¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦1.1¦0¦0¦0¦0¦0
14 | TrueNorthPower Arrow 2m1kw | Wind Arrow 1kw | 1.23 |  |  | 2 | 2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.015¦0.04¦0.08¦0.14¦0.22¦0.35¦0.5¦0.67¦0.88¦1.04¦1.18¦1.23¦0.5¦0.5¦0.52¦0.52¦0.52¦0.53¦0.54¦0.55¦0¦0¦0¦0¦0¦0¦0¦0
15 | Bergey BWCXL1 2.5m 1kw | BWC XL.1 | 1.234 |  |  | 2 | 2.5 | No | No | N/A |  | 11, 15 |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.023¦0.059¦0.129¦0.23¦0.375¦0.531¦0.703¦0.89¦1.077¦1.21¦1.234¦1.202¦1.14¦1.089¦1.035¦0.988¦0.937¦0.89¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
16 | African Wind Power AWP3.6(Grid tie) 3.6m 1.6kw | AWP 3.6m | 1.32 |  |  | 3 | 3.6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.14¦0.26¦0.43¦0.65¦0.85¦1.05¦1.23¦1.32¦1.31¦1.2¦1.05¦0.9¦0.75¦0.6¦0.45¦0.3¦0.15¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
17 | Fortis Passaat 3.12m 1,4kW | Passaat | 1.4 |  |  | 3 | 3.12 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.045¦0.11¦0.22¦0.36¦0.46¦0.6¦0.73¦0.87¦1.02¦1.15¦1.28¦1.37¦1.4¦1.4¦1.4¦1.38¦1.35¦1.3¦1.25¦1.21¦1.18¦1.16¦0¦0¦0¦0¦0
18 | Future Energy FE1048U 1.8m 1kW | FE1048U | 1.5 |  |  | 1 | 1.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.053¦0.1¦0.17¦0.28¦0.41¦0.59¦0.79¦0.93¦1.06¦1.23¦1.47¦1.5¦1.5¦1.5¦1.5¦1.5¦1.5¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
19 | Future Energy FE1048U 1.8m 1kw | FE1048U | 1.5 |  |  | 1 | 1.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦0.051¦0.079¦0.115¦0.158¦0.207¦0.245¦0.317¦0.403¦0.508¦0.608¦0.756¦0.906¦1.065¦1.215¦1.35¦1.45¦1.5¦1.5¦1.5¦1.5¦1.5¦0¦0¦0¦0¦0
20 | Zephyr Airdolphin 1.8m 1kW | Zephyr Airdolphin | 1.523 |  |  | 1 | 1.8 | unknown | Past | unknown |  |  | PNNL does not have documentation | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.021¦0.059¦0.097¦0.185¦0.285¦0.399¦0.546¦0.739¦0.923¦1.137¦1.372¦1.507¦1.523¦1.419¦1.347¦1.33¦1.351¦1.385¦1.372¦1.414¦1.427¦1.444¦0¦0¦0¦0¦0
21 | Joliet Cyclone 1 2.7m 1kw | Joliet Cyclone 1 | 1.64 |  |  | 2 | 2.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.03¦0.08¦0.15¦0.21¦0.27¦0.36¦0.45¦0.58¦0.75¦1.01¦1.19¦1.39¦1.64¦1.03¦0.84¦0.67¦0.53¦0.41¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
22 | Joliet Ultra X900 3m 1kw | Joliet Ultra X900 | 1.66 |  |  | 3 | 3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.03¦0.08¦0.16¦0.21¦0.27¦0.35¦0.46¦0.6¦0.77¦1¦1.18¦1.4¦1.66¦1.04¦0.83¦0.68¦0.53¦0.4¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
23 | Sonkyo Energy Windspot 1.5kW 4.05m | Windspot 1.5kW | 1.68 |  |  | 4 | 4.05 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.08¦0.163¦0.3¦0.48¦0.68¦0.9¦1.14¦1.34¦1.55¦1.64¦1.68¦1.66¦1.62¦1.58¦1.57¦1.57¦1.58¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
24 | Hummer 3.1m 1kw | Hummer 1kW | 2 |  |  | 3 | 3.1 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.105¦0.205¦0.35¦0.55¦0.79¦1.05¦1.3¦1.47¦1.83¦1.95¦2¦1.92¦1.86¦1.78¦1.7¦1.6¦1.5¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
25 | Travere Industries 6m 2.1kW | Travere 2.1 kW | 2.1 |  |  | 6 | 6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.14¦0.33¦0.65¦1.12¦1.78¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1¦2.1
26 | Energy Ball HEA V200 1.98m 2.5kW | Energy Ball V200 | 2.23 |  |  | 2 | 1.98 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.02¦0.06¦0.11¦0.16¦0.25¦0.39¦0.56¦0.74¦0.91¦1.1¦1.32¦1.6¦1.93¦2.23¦2.23¦2.23¦2.23¦2.23¦2.23¦0¦0¦0¦0¦0¦0¦0¦0
27 | Pinnacle-Tech Caravel 2.5kW 3.5m | Caravel 2.5 | 2.4 |  |  | 3 | 3.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.1¦0.25¦0.46¦0.72¦1.14¦1.6¦2¦2.17¦2.22¦2.35¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦2.4¦0¦0¦0¦0¦0
28 | SkyStream 2.4 | SkyStream 2.4 | 2.4 |  |  | 3.7 | 3.7 | No | No | N/A |  | 28, 29, 30, 34 | DELETE | 0 | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦31¦32¦33¦34¦35¦36¦37¦38¦39¦40 | 0¦0¦0¦0¦0.08¦0.2¦0.35¦0.6¦1¦1.6¦2¦2.25¦2.35¦2.4¦2.4¦2.37¦2.3¦2.09¦2¦2¦2¦2¦2¦1.98¦1.95¦1.8¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
29 | Southwest Windpower Skystream 3.7m 1.9kw | skystream 3.7 | 2.425 |  |  | 3 | 3.7 | No | No | N/A |  | 28, 29, 30, 34 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.084¦0.203¦0.391¦0.643¦0.968¦1.333¦1.748¦2.106¦2.301¦2.403¦2.425¦2.414¦2.4¦2.3¦2.265¦2.203¦2.203¦2.203¦2.203¦2.203¦2.203¦2.203¦0¦0¦0¦0¦0
30 | Xzeres Skystream 3.7m 1.9kw | Skystream 3.7 | 2.425 | 2.4 | 2.1 | 3 | 3.7 | No | Yes | 2020-01-01 | SWCC | 28, 29, 30, 34 |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.084¦0.203¦0.391¦0.643¦0.968¦1.333¦1.748¦2.106¦2.301¦2.403¦2.425¦2.414¦2.4¦2.3¦2.265¦2.203¦2.203¦2.203¦2.203¦2.203¦2.203¦2.203¦0¦0¦0¦0¦0
31 | NREL 2.5kW Distributed Residential Turbine Reference | NREL | 2.5 |  |  | 1.85 |  | No | No | N/A |  |  |  | unknown | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25 | 0¦0¦0¦0.070542773¦0.1672125¦0.326586914¦0.564342188¦0.896154492¦1.3377¦1.904654883¦2.5¦2.5¦2.5¦2.5¦2.5¦2.5¦2.5¦2.5¦2.5¦0¦0¦0¦0¦0¦0¦0
32 | Xzeres 110 | Xzeres 110 | 2.5 |  |  | 3.6 | 3.7 | No | No | N/A |  |  |  | 0 | 0¦2.2¦4.5¦6.7¦8.9¦11.2¦13.4¦13.9¦40 | 0¦0¦0.125¦0.6¦1.6¦2.5¦2.5¦0¦0
33 | Wind Energy Solutions WES5 5m 2.5kw Tulipo | WES5 Tulipo | 2.625 |  |  | 5 | 5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.068¦0.243¦0.53¦0.958¦1.553¦2.159¦2.474¦2.595¦2.625¦2.598¦2.552¦2.382¦2.192¦1.96¦1.768¦1.495¦1.31¦1.055¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
34 | Southwest Windpower Skystream 3.7m 1.9kw | Skystream 3.7 | 2.63 |  |  | 3 | 3.7 | No | No | N/A |  | 28, 29, 30, 34 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.12¦0.27¦0.48¦0.74¦1.12¦1.6¦2.1¦2.35¦2.53¦2.63¦2.63¦2.6¦2.44¦2.23¦2.1¦2.05¦2.05¦2.05¦2.05¦2.05¦2.05¦2.05¦0¦0¦0¦0¦0
35 | Samrey Merlin_3.5m_3kw | Samrey Merlin | 2.7 |  |  | 3 | 3.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.1¦0.21¦0.36¦0.57¦0.85¦1.2¦1.6¦1.9¦2.2¦2.4¦2.5¦2.6¦2.65¦2.7¦2.7¦2.7¦2.7¦2.7¦2.7¦2.7¦2.7¦2.7¦0¦0¦0¦0¦0
36 | Joliet Cyclone 2 3.2m 2.3kw | Joliet Cyclone 2 | 2.9 |  |  | 3 | 3.2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.04¦0.1¦0.16¦0.24¦0.35¦0.49¦0.69¦0.99¦1.39¦1.99¦2.4¦2.9¦2.82¦2.29¦1.83¦1.47¦1.15¦0.98¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
37 | Kingspan-Proven Kingspan KW3 3.8m 2.5kW | KW3 2.5kW | 2.9 |  |  | 3 | 3.8 | unknown | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.078¦0.217¦0.459¦0.81¦1.2¦1.49¦1.84¦2.13¦2.41¦2.58¦2.7¦2.83¦2.9¦2.9¦2.89¦2.78¦2.76¦2.76¦2.76¦2.76¦2.76¦2.76¦2.76¦2.76¦2.76¦2.76¦2.76
38 | Kestrel e400i | Kestrel e400i | 3 |  |  | 4 | 4 | No | No | N/A |  |  | Don't know about this model, but Kestrel has a 3.5 kW. | 0 | 0¦1¦2¦2.5¦3¦3.5¦4¦4.5¦5¦5.5¦6¦6.5¦7¦7.5¦8¦8.5¦9¦9.5¦10¦10.5¦11¦11.5¦12¦25¦26¦40 | 0¦0¦0.023¦0.045¦0.078¦0.123¦0.185¦0.263¦0.361¦0.481¦0.624¦0.794¦0.991¦1.219¦1.480¦1.775¦2.108¦2.479¦2.891¦3.050¦3.120¦3.150¦3.150¦3.150¦0¦0
39 | Travere Industries Travere 3.6m 3kW | Travere 3.6m | 3 |  |  | 3 | 3.6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.14¦0.27¦0.46¦0.73¦1.1¦1.56¦2.14¦2.85¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3¦3
40 | Whisper 500 (H175) (WPT 3000) | Whisper 500 | 3 |  |  | 4 | 4.26 | No | No | N/A |  |  |  | 0 | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦31¦32¦33¦34¦35¦36¦37¦38¦39¦40 | 0¦0¦0¦0¦0.16¦0.39¦0.72¦0.99¦1.41¦1.86¦2.52¦3.12¦3.39¦3.54¦3.6¦3.54¦3.48¦3.33¦3.27¦3.21¦3.12¦3.12¦3.12¦3.12¦3.12¦3.12¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
41 | Westwind 3.7m 3kw | Westwind 3.7m 3kw | 3.1 |  |  | 3 | 3.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.06¦0.16¦0.32¦0.51¦0.81¦1.2¦1.5¦2¦2.4¦2.7¦3¦3.1¦3.1¦3¦3¦3¦3¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
42 | Ennera Windera S 4.36m 3.2KW | Windera S | 3.129 |  |  | 4 | 4.36 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.0152¦0.404¦0.768¦1.295¦1.896¦2.472¦2.907¦3.129¦3.127¦3.003¦2.651¦2.3¦1.95¦1.6¦1.25¦0.9¦0.55¦0.2¦0¦0¦0¦0¦0¦0¦0¦0¦0
43 | Hummer 3.8m 2kW | H3.8-2kW | 3.2 |  |  | 3 | 3.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.18¦0.4¦0.72¦1.1¦1.65¦2.1¦2.56¦2.8¦2.94¦3.11¦3.2¦3.2¦3.14¦3.08¦3.02¦2.98¦2.94¦2.89¦2.84¦2.79¦2.74¦2.69¦0¦0¦0¦0¦0
44 | Kestrel 400i 4m 3kW | Kestrel 400i | 3.2 |  |  | 4 | 4 | No | No | N/A |  |  | Don't know about this model, but Kestrel has a 3.5 kW. | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.12¦0.27¦0.48¦0.8¦1.15¦1.56¦2.01¦2.5¦2.9¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦3.2¦0¦0¦0¦0¦0
45 | ReDriven 3.8m 3kw | ReDriven 3.8m | 3.327 |  |  | 3 | 3.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.1¦0.25¦0.502¦0.722¦1.036¦1.632¦2.527¦3.17¦3.327¦3.327¦3.327¦3.327¦3.327¦3.327¦3.312¦3.312¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
46 | ReDriven 3.8m 3kw | ReDriven 3.8m | 3.327 |  |  | 3 | 3.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.0562¦0.134¦0.261¦0.45¦0.715¦1.067¦1.52¦2.083¦2.77¦3.327¦3.327¦3.327¦3.327¦3.327¦3.312¦3.312¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
47 | Joliet Cyclone 3 4.5m 3kw | Joliet Cyclone 3kW | 3.96 |  |  | 4 | 4.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.09¦0.22¦0.43¦0.73¦1.04¦1.5¦2.13¦3.02¦3.46¦3.96¦3.63¦2.91¦2.3¦1.84¦1.5¦1.11¦0.55¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
48 | Anelion SW3.5GT 5kW 3.5m | Anelion SW3.5-GT | 4 |  |  | 3 | 3.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.1¦0.24¦0.437¦0.733¦1.18¦1.66¦2.29¦2.9¦3.56¦4¦4¦4¦3.8¦3.3¦2.8¦2.3¦1.8¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
49 | Sonkyo Energy Windspot 3.5kW 4.05m | Windspot 3.5kW | 4.17 |  |  | 4 | 4.05 | No | Past | unknown |  | 49, 50 | PNNL does not have documentation. | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.077¦0.28¦0.56¦0.88¦1.299¦1.82¦2.48¦3.25¦3.73¦3.91¦4.01¦4.06¦4.121¦4.17¦4.17¦4.17¦4.17¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
50 | Sonkyo Energy Windspot 3.5kW 4.05m | Windspot 3.5kW | 4.17 |  |  | 4 | 4.05 | No | Past | unknown |  | 49, 50 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.0875¦0.282¦0.563¦0.877¦1.283¦1.796¦2.477¦3.214¦3.697¦3.876¦3.967¦4.031¦4.096¦4.142¦4.17¦4.17¦4.17¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
51 | Fortis Montana 5m 5kW | Fortis Montana | 4.48 |  |  | 5 | 5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.07¦0.18¦0.4¦0.69¦1.11¦1.63¦2.17¦2.76¦3.3¦3.82¦4.22¦4.48¦4.38¦4.27¦4.01¦3.7¦3.55¦3.51¦3.56¦3.56¦3.56¦3.56¦3.56¦0¦0¦0¦0¦0
52 | Zhejiang Huaying HY5-AD5.6 5.6m 5kW | HY5-AD5.6 | 4.85 |  |  | 5 | 5.6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.21¦0.62¦1.12¦1.74¦2.53¦3.34¦3.69¦4.05¦4.14¦4.18¦4.27¦4.5¦4.68¦4.69¦4.37¦4.77¦4.31¦4.85¦0¦4.75¦0¦4.39¦0¦0¦0¦0¦0
53 | Endurance Wind S-250 | Endurance S-250 | 5 |  |  | 5.5 | 5.5 | No | No | N/A |  |  |  | 0 | 0¦2¦4¦6¦8¦10¦12¦14¦16¦18¦20¦21¦40 | 0¦0¦0¦0.9¦2.05¦3.9¦4.8¦5¦4.55¦4¦3.5¦0¦0
54 | Endurance Wind S-343 | Endurance S-343 | 5 | 5 | 5.4 | 6.37 | 6.37 | No | Past | 2014-02-24 | SWCC | 54, 57 |  | 0 | 0¦2¦4¦6¦8¦10¦12¦14¦16¦18¦20¦21¦40 | 0¦0¦0¦1.15¦3.2¦4.9¦5.3¦4.95¦3.85¦3¦1¦0¦0
55 | Evance R9000 | Evance R9000 | 5 | 5 | 4.7 | 5.5 | 5.5 | unknown | Past | 2012-12-03 | UK MCS | 55, 56 | No known recent sales in US, but may be available in UK. | 0 | 0¦2¦4¦6¦8¦10¦12¦14¦16¦18¦20¦21¦40 | 0¦0¦0.2¦1.0¦2.5¦4¦4.9¦5.05¦5.1¦5.1¦5.1¦0¦0
56 | Evance R-9000 5.5m 5kw | Evance R9000 | 5.242 |  |  | 5 | 5.5 | No | Past | unknown |  | 55, 56 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.21¦0.576¦1.104¦1.783¦2.542¦3.349¦4.077¦4.628¦4.911¦5.066¦5.141¦5.142¦5.159¦5.217¦5.212¦5.242¦5.235¦5.235¦5.235¦5.235¦5.235¦5.235¦5.235¦5.235¦5.235¦5.235¦5.235
57 | Endurance S-343 6.4m 5Kw | Endurance S-343 | 5.424 |  |  | 6 | 6.4 | No | Past | unknown |  | 54, 57 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦0.533¦1.199¦2.201¦3.258¦4.146¦4.79¦5.219¦5.424¦5.331¦4.919¦4.35¦3.826¦3.472¦3.027¦2.7¦2.4¦2.1¦1.8¦1.5¦1.2¦0¦0¦0¦0¦0¦0
58 | ReDriven 6.5m 5kw | ReDriven 6.5m | 5.548 |  |  | 6 | 6.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.31¦0.643¦1¦1.429¦2.024¦2.952¦4.167¦5.238¦5.548¦5.524¦5.524¦5.548¦5.548¦5.548¦5.548¦5.548¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
59 | ReDriven 6.5m 5kw | ReDriven 6.5m | 5.55 |  |  | 6 | 6.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.19¦0.45¦0.89¦1.43¦2.02¦2.95¦4.17¦5.24¦5.54¦5.55¦5.55¦5.55¦5.55¦5.55¦5.55¦5.55¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
60 | Ampair 6000 5.5m 6kw | Ampair 6000 | 6 |  |  | 5 | 5.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.31¦0.5¦0.99¦1.51¦2.4¦3.2¦4.51¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
61 | C&F Green Energy CF6d 6m 6kW | CF6d | 6 |  |  | 6 | 6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.1¦0.4¦0.83¦1.45¦2.3¦3.4¦4.8¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6
62 | C&F Green Energy CF6e 8m 6kW | CF6d | 6 |  |  | 8 | 8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.32¦0.75¦1.48¦2.5¦3.98¦5.92¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦6¦0¦0¦0¦0¦0
63 | Eoltec Scirocco E5.6m-6kw | Eoltec Scirocco E5 | 6 |  |  | 5 | 5.6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.05¦0.28¦0.66¦1.22¦1.98¦2.92¦4.02¦5.06¦5.72¦6¦6¦5.8¦5.6¦5.4¦5.3¦5.2¦5.1¦5¦5¦5¦5¦5¦5¦0¦0¦0¦0¦0
64 | Westwind 5.5m 6kW | Westwind 5.5 | 6.11 |  |  | 5 | 5.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.07¦0.22¦0.64¦1.22¦1.99¦2.92¦3.99¦5.07¦5.57¦5.79¦5.91¦6.11¦5.78¦5.22¦5.02¦5¦5.02¦5.03¦5.03¦5.03¦5.03¦5.03¦5.03¦0¦0¦0¦0¦0
65 | Kingspan-Proven Kingspan KW6 5.6m 6kW SD Wind Energy SD6 | KW6 SD6 | 6.136 | 6 | 5.2 | 5 | 5.6 | Yes | Yes | 2020-07-01 | SWCC |  | This turbine model is now owned by SD Wind Energy. | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.172¦0.485¦1.02¦1.733¦2.674¦3.546¦4.428¦5.164¦5.626¦5.96¦6.026¦6.059¦6.099¦6.136¦6.1¦5.952¦5.988¦5.8¦5.8¦5.8¦5.8¦5.8¦5.8¦5.8¦5.8¦5.8¦5.8
66 | Aventa AV-7 12.9m 6.5kW | Aventa AV-7 | 6.253 |  |  | 12 | 12.9 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.638¦1.549¦3.117¦5.87¦6.234¦6.234¦6.253¦6.234¦6.234¦6.253¦6.234¦6.216¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
67 | WindEnergyLebanon 5kW 6m | WindEnergyLebanon 5kW 6m | 6.37 |  |  | 6 | 6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.33¦0.72¦1.21¦1.73¦2.46¦3.53¦5¦5.64¦6.37¦5.75¦4.6¦3.72¦2.95¦2.36¦1.76¦0.94¦0.04¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
68 | Joliet Cyclone 5 6.4m 5kw | Joliet Cyclone 5 | 6.4 |  |  | 6 | 6.4 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.17¦0.44¦0.82¦1.19¦1.7¦2.47¦3.54¦5.04¦5.67¦6.4¦5.75¦4.59¦3.66¦2.95¦2.35¦1.79¦0.85¦0.03¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
69 | Pinnacle-Tech Frigate 7.5kW 6m | FD6-7.5 | 7.7 |  |  | 6 | 6 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.32¦0.61¦1.1¦1.6¦2.5¦3.7¦5.3¦6.5¦7.4¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7¦7.7
70 | Hummer 6.4m 5kw | H6.4-5KW | 7.75 |  |  | 6 | 6.4 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.16¦0.46¦0.93¦1.46¦2¦3¦4.32¦5.15¦6.1¦6.82¦7.24¦7.54¦7.75¦7.5¦7.2¦6.9¦6.6¦6.25¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
71 | Windspot 7.5kW 6.3m | Windspot 7.5 kW | 8.02 |  |  | 6 | 6.3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.43¦0.9¦1.55¦2.37¦3.4¦4.4¦5.4¦6.53¦7.46¦7.92¦8.02¦8.02¦7.88¦7.68¦7.51¦7.51¦7.54¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
72 | Bergey Excel - S.60 | Excel- S60 | 10 |  |  | 6 | [6 empty] | DELETE | 0 | 0¦0.5¦1¦1.5¦2¦2.5¦3¦3.5¦4¦4.5¦5¦5.5¦6¦6.5¦7¦7.5¦8¦8.5¦9¦9.5¦10¦10.5¦11¦11.5¦12¦12.5¦13¦13.5¦14¦14.5¦15¦15.5¦16¦16.5¦17¦17.5¦18¦18.5¦19¦19.5¦20¦20.5¦21¦21.5¦22¦22.5¦23¦23.5¦24¦24.5¦25¦25.5¦26¦26.5¦27¦27.5¦28¦28.5¦29¦29.5¦30¦30.5¦31¦31.5¦32¦32.5¦33¦33.5¦34¦34.5¦35¦35.5¦36¦36.5¦37¦37.5¦38¦38.5¦39¦39.5¦40 | 0¦0¦0¦0¦0¦0¦0.05¦0.25¦0.45¦0.55¦0.85¦1.25¦1.5¦2¦2.5¦3.05¦3.6¦4.25¦5.1¦6¦6.9¦7.9¦8.9¦10¦10.9¦11.65¦12¦12.4¦12.45¦12.475¦12.5¦12.5¦12.5¦12.5¦12.5¦12.5¦12.475¦12.45¦12.25¦11.9¦12¦11.5¦5¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
73 | Evoco 10kW 9.7m | Evoco 10kW | 10 |  |  | 9 | 9.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.6¦1.6¦2.9¦4.6¦6.7¦8.2¦9¦9.6¦9.9¦10¦10¦9.8¦9.8¦9.8¦9.7¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6¦9.6
74 | Pinnacle-Tech Frigate 10kW 7m | FD7-10/11 | 10.4 |  |  | 7 | 7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦0.8¦1.5¦2.3¦3.3¦5¦7.4¦9.6¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4¦10.4
75 | Aircon10S 7.54m 10kW | Aircon10S | 10.99 |  |  | 7 | 7.45 | No | Past | unknown |  |  | PNNL does not have documentation | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.312¦1.12¦2.203¦3.6¦5.159¦6.892¦8.5¦9.61¦10.31¦10.57¦10.6¦10.6¦10.6¦10.74¦10.94¦10.99¦10.99¦10.99¦10.99¦10.99¦10.99¦10.99¦0¦0¦0¦0¦0
76 | Gaia Wind 133 - 11kw | Gaia 133-11kW | 11 | 11 | 10.7 | 13 | 13 | No | Past | 2010-10-07 | UK MCS | 76, 79, 85 |  | 0 | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11.02¦12.02¦12.97¦14.06¦14.98¦16¦16.98¦17.89¦19.5¦40 | 0¦0¦0¦0¦0.71¦2.46¦4.43¦6.3¦7.91¦9.16¦10.29¦10.69¦10.93¦10.74¦10.26¦9.54¦8.79¦8.76¦3¦0¦0
77 | C&F Green Energy CF11 9m 11kW | CF11 | 11.1 |  |  | 9 | 9 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.02¦0.56¦1.43¦2.64¦4.28¦6.37¦8.66¦10.5¦11.02¦11.1¦11.08¦11.03¦10.87¦11¦11¦11¦11¦11¦11¦11¦11¦11¦11¦0¦0¦0¦0¦0
78 | Westwind 6.4m 10kW | Westwind 10kW | 11.48 |  |  | 6 | 6.4 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.08¦0.172¦0.75¦1.62¦2.57¦3.81¦5.42¦7.19¦9.17¦10.62¦11.33¦11.3¦11.48¦11.12¦10.71¦10.59¦10.79¦10.7¦10.7¦10.7¦10.7¦10.7¦10.7¦0¦0¦0¦0¦0
79 | Gaia Wind 13m 11kw | Gaia 133-11kW | 11.79 |  |  | 13 | 13 | No | Past | unknown |  | 76, 79, 85 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦1.1¦2.8¦5¦7.3¦8.9¦10.4¦11.4¦11.79¦11.4¦10.96¦10.07¦9.35¦8.96¦8.96¦8.8¦8.47¦8.08¦7.75¦7.47¦7.19¦6.81¦6.42¦0¦0¦0¦0¦0
80 | Xzeres 442SR | Xzeres 442SR | 12 | 10 | 10.4 | 7.2 | 7.2 | No | Past | unknown | unavailable |  | This turbine model was definitely certified by SWCC, but PNNL cannot find the (old) documentation! We could ask SWCC, but it is no longer sold. | 0 | 0¦2.2¦4.5¦6.7¦8.9¦11.2¦12.5¦13.4¦14.8¦17.9¦18.8¦40 | 0¦0¦0.7¦2.6¦6¦10¦11.9¦12¦12¦12¦0¦0
81 | Bergey Excel-10 7m 10kw | Bergey Excel 10 | 12.546 | 10 | 8.9 | 7 | 7 | Yes | Yes | 2020-12-01 | SWCC |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.102¦0.399¦0.848¦1.51¦2.403¦3.602¦5.071¦6.856¦8.863¦10.885¦12.019¦12.395¦12.495¦12.546¦12.503¦12.442¦12.208¦11.989¦11.6¦11.2¦10.8¦10.4¦10¦9.6¦9.2¦8.8¦8.4¦8
82 | Future Energy Airforce10 8m 13kW | Airforce10 | 13 |  |  | 8 | 8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.15¦0.6¦1.33¦2.38¦3.84¦5.81¦8.36¦11.5¦12.7¦13¦13¦13¦13¦13¦13¦13¦13¦13¦13¦13¦13¦13¦13¦0¦0¦0¦0¦0
83 | Joliet Cyclone 10 8m 10kw | Joliet Cyclone 10 | 13.02 |  |  | 8 | 8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.7¦1.36¦2.39¦3.31¦4.88¦6.95¦9.98¦11.4¦13.02¦11.83¦9.33¦7.49¦6.02¦4.83¦3.58¦1.84¦0.05¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
84 | Hummer 8m 10kw | Hummer 10kW | 14.88 |  |  | 8 | 8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.16¦0.82¦2.17¦4¦6.06¦8.08¦9.48¦11.65¦13.02¦14.03¦14.73¦14.88¦14.5¦13.91¦13.25¦12.47¦11.81¦11.15¦10.72¦10.06¦9.56¦9.05¦0¦0¦0¦0¦0
85 | Gaia Wind 13m 11kw | Gaia 133-11kW | 15 |  |  | 13 | 13 | No | Past | unknown |  | 76, 79, 85 | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.31¦2.28¦5¦7.57¦9.8¦11.67¦13.12¦14.15¦14.8¦15¦14.8¦14.4¦14.42¦14.24¦14.08¦14¦13.74¦13.7¦13.7¦13.7¦13.7¦13.7¦0¦0¦0¦0¦0
86 | C&F Energy CF15e 13.1m 15kW | CF15e | 15.2 |  |  | 13 | 13.1 | Yes | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.9¦2.1¦3.8¦6.9¦11.1¦15.2¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦15.1¦0¦0¦0¦0¦0
87 | C&F GreenEnergy CF15 11.1m 15kw | CF15 | 16.32 |  |  | 11 | 11.1 | Yes | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.3¦0.98¦2.1¦3.55¦5.37¦7.78¦11.02¦14.38¦15.3¦15.14¦15.5¦15.82¦16.07¦16.03¦15.75¦16.32¦16¦16¦16¦16¦16¦16¦16¦0¦0¦0¦0¦0
88 | Wind Turbine Industries Corp Jacobs 29-20 | 29-20 | 17.5 |  |  | 8 | 8.8 | No | No | N/A |  |  |  | 0 | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦31¦32¦33¦34¦35¦36¦37¦38¦39¦40 | 0¦0¦0¦0¦0.7¦1.3¦2.3¦3.4¦5.1¦7.4¦10.3¦13.7¦17.5¦17.5¦17.5¦17.1¦6.1¦5.4¦5.4¦5.4¦5.4¦5.4¦5.4¦5.4¦5.4¦5.4¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
89 | Wind Turbine Industries Corp Jacobs 31-20 | Jacobs 31-20 | 20 | 20 | 12 | 9.45 | 9.5 | No | Past | 2012-03-20 | Intertek |  |  | 0 | 0¦1¦2¦3¦3.35¦4¦5¦6¦7¦8¦9¦10¦11¦11.62¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦31¦40 | 0¦0¦0¦0¦0¦0¦1.59¦2.75¦4.37¦6.53¦9.29¦12.75¦16.97¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦20¦0¦0
90 | C&F Green Energy CF20 12.8m 20kW | CF20 | 21.3 |  |  | 13 | 12.8 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.51¦1.3¦2.95¦5.55¦8.5¦12.65¦17.48¦20.24¦20.56¦20.75¦20.47¦20.57¦20.58¦20.84¦20.82¦21.3¦21¦21¦21¦21¦21¦21¦21¦0¦0¦0¦0¦0
91 | Coemi Skywing G-3 20kW 15m | Skywing G-3 | 21.5 |  |  | 15 | 15 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2.8¦4.3¦5.9¦7.5¦9.9¦12.7¦15.9¦19¦20.9¦21.5¦21.5¦21.5¦21.47¦21.5¦21.5¦21.5¦21.5¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
92 | ReDriven 12.3m 20kw | ReDriven 12.3m | 22.159 |  |  | 12 | 12.3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦1.15¦2.273¦3.598¦5.682¦8.049¦10.985¦15.057¦18.466¦21.023¦22.064¦22.159¦22.159¦22.159¦22.064¦22.064¦22.064¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
93 | ReDriven 12.3m 20kw | ReDriven 12.3m | 22.159 |  |  | 12 | 12.3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.69¦1.63¦3.18¦5.5¦8.049¦10.985¦15.057¦18.466¦21.023¦22.064¦22.159¦22.159¦22.159¦22.064¦22.064¦22.064¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
94 | Westwind 10.2m 20kw | Westwind 10.2m 20kw | 22.75 |  |  | 10 | 10.2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.15¦0.86¦1.86¦3.25¦5.29¦7.76¦10.79¦13.55¦15.68¦17.33¦18.79¦20.03¦20.57¦21.15¦21.79¦22.11¦22.75¦22.75¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
95 | Joliet Cyclone 20 10m 20kw | Joliet Cyclone 20 | 25.93 |  |  | 10 | 10 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦1.2¦2.4¦4.15¦6.86¦10¦13.95¦19¦22.91¦25.93¦23.49¦18.72¦15¦12.09¦9.65¦7.44¦3.95¦0.35¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
96 | Eocycle EO25/12 12.6m 25kW | E025 | 27.64 | 25 | 28.9 | 12 | 15.81 | Yes | Yes | 2020-03-21 | SGS |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0.96¦2.82¦5.7¦9.81¦15.25¦20.53¦23.51¦25¦25.95¦26.6¦27.2¦27.56¦27.64¦27.31¦26.37¦24.77¦21.68¦17.17¦13.19¦10.83¦11.33¦12.16¦0¦0¦0¦0¦0
97 | Pitchwind 14m 30kW | Pitchwind 14m 30kW | 30 |  |  | 14 | 14 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.3¦1.6¦3.9¦7.3¦11.8¦17.6¦22.7¦26.2¦28.4¦29.3¦29.7¦29.8¦29.9¦30¦30¦30¦30¦30¦30¦30¦30¦30¦30¦30¦30¦30¦30¦30
98 | Endurance G-3120 19.2m 35Kw | G-3120 | 35 |  |  | 19 |  | No | No | N/A |  |  | DELETE | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦8.1¦15.2¦24.8¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦35¦0¦0¦0¦0¦0
99 | Energie PGE 20/35 19.2m 35kW | Energie PGE 20/35 | 36.4 |  |  | 19 | 19.2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦4.2¦9.1¦15.4¦21.7¦27.1¦30.9¦33.7¦35.5¦36¦36.3¦36.4¦35.9¦34.6¦31.9¦30¦30¦30¦30¦30¦30¦30¦30¦0¦0¦0¦0¦0
100 | Endurance Wind E-3120 | E-3120 | 50 | 50 | 56 | 19.2 | 19.2 | No | Past | 2013 | SWCC |  |  | 0 | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦40 | 0¦0¦0¦0¦2¦9¦15¦25¦36¦44¦51¦55¦57¦59.5¦59¦58¦57¦55¦50¦44¦37¦0¦0
101 | Ergycon Ely50 20.7m | Ely50 | 50.5 |  |  | 20 | 20.7 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦2.2¦4.9¦9.4¦15.9¦32.7¦48.8¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦50.5¦0¦0¦0¦0¦0
102 | C&F Green Energy CF50 20m 50kw | CF50 | 52 |  |  | 20 | 20 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦1.5¦4.7¦9.2¦15.9¦24.2¦37.4¦52¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50¦50
103 | Energie PGE 20/50 19.2m 50kW | Energie PGE 20/50 | 53.5 |  |  | 19 | 19.2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2¦5.8¦14.3¦25.3¦33.8¦41.3¦46.5¦50.9¦52.9¦53.5¦51.7¦49.7¦47.6¦46¦45¦45¦45¦45¦45¦45¦45¦45¦0¦0¦0¦0¦0
104 | Aeolos 18m 50kW | Aeolos-H 50kW | 53.7 |  |  | 18 | 18 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2.27¦5.6¦10.7¦17.7¦25.7¦37.6¦52.7¦53.7¦50.7¦49¦48¦49.1¦49¦46.4¦46.1¦45.4¦45¦45¦45¦45¦45¦45¦0¦0¦0¦0¦0
105 | Atlantic Orient Canada 15/50 15m 50kW 50Hz | AOC 15/50 | 53.841 |  |  | 15 | 15 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦2.328¦6.785¦14.27¦21.933¦29.953¦37.438¦44.567¦49.736¦52.946¦53.841¦52.42¦52.5¦52.5¦52.5¦52.5¦52.5¦52.5¦52.5¦0¦0¦0¦0¦0¦0¦0¦0
106 | Aria S.R.L Libellula 18m 55kW | Libellula 55kW | 55 |  |  | 18 | 18 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦1.7¦4.8¦9.6¦15.8¦25.1¦36.3¦47.9¦55¦55¦55¦55¦55¦55¦55¦55¦55¦55¦55¦55¦55¦55¦55¦0¦0¦0¦0¦0
107 | ReDriven 14.3m 50kw | ReDriven 14.3m | 55.3 |  |  | 14 | 14.3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦1.3¦3.5¦7.22¦12¦18.06¦24.72¦33.05¦43.61¦52.5¦55.3¦55.23¦55.3¦55.3¦55.3¦55.3¦55.3¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
108 | ReDriven 14.3m 50kw | ReDriven 14.3m | 55.3 |  |  | 14 | 14.3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.93¦2.21¦4.3¦7.44¦11.8¦17.65¦25.1¦34.4¦45.78¦55.3¦55.23¦55.3¦55.3¦55.3¦55.3¦55.3¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
109 | Coemi G-3 15.2m 50kW | Coemi 55/15 | 57.4 |  |  | 15 | 15.2 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.4¦1.8¦4¦8¦15.6¦26¦38¦49¦55.4¦57.4¦57.4¦57.4¦56¦54.7¦53.6¦52.3¦50.8¦50.6¦50.4¦50.4¦51.1¦52.1¦53¦54¦0¦0¦0¦0
110 | Harbon HWT60 15.93m 60kW | HWT60 | 58.7 |  |  | 15 | 15.93 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2.1¦5.1¦9.6¦15.8¦24.2¦32.7¦47.8¦54.9¦58.6¦58.7¦58¦57.5¦57¦56.5¦55.7¦55¦54¦52¦50¦48¦46¦44¦0¦0¦0¦0¦0
111 | Deimos DT2160 21m 60kW | DT2160 | 60 |  |  | 21 | 21 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦2.3¦5.7¦11¦19¦30¦45¦60¦60¦60¦60¦60¦60¦60¦60¦60¦60¦60¦60¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
112 | Seaforth Energy AOC 15-50 Wind Turbine | AOC 15-50 | 63 |  |  | 15 | 15 | No | No | N/A |  |  |  | Unknown | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦31¦32¦33¦34¦35¦36¦37¦38¦39¦40 | 0¦0¦0¦0¦0¦4.4¦8.9¦15.6¦24.4¦33¦44¦50¦55¦58¦62¦64¦66¦65¦64¦64¦64¦63¦63¦63¦63¦63¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
113 | Greenstorm 60kW 22.3m | GS 21 S | 64.1 |  |  | 22 | 22.3 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦6.2¦11.3¦19.3¦29.3¦41.6¦58.7¦61.7¦61.1¦63¦64.1¦62¦60.7¦61.8¦63.1¦61.8¦60.7¦63.1¦61.9¦62.1¦63.6¦61.9¦60.8¦0¦0¦0¦0¦0
114 | Atlantic Orient Canada AOC 15/50 15m 50kw 60Hz | AOC 15-50 | 65.07 |  |  | 15 | 15 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦0¦2.84¦7.3¦16.62¦22.55¦31.75¦40.41¦45.02¦51.63¦59.99¦60.37¦61.79¦62.28¦65.07¦64.8¦63.32¦59.34¦40.02¦0¦0¦0¦0¦0¦0¦0¦0
115 | Atlantic Orient Canada 15/50 15m 50kW 60Hz | AOC 15-50 | 65.435 |  |  | 15 | 15 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦1.794¦4.826¦11.064¦18.371¦25.678¦33.875¦41.36¦48.311¦53.659¦59.541¦61.326¦63.646¦64.897¦65.435¦64.905¦63.662¦63.666¦62.602¦0¦0¦0¦0¦0¦0¦0¦0
116 | Wind Energy Solutions WES18 18m 80kw | WES18 | 83.3 |  |  | 18 | 18 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2.9¦6¦11¦17.7¦27.3¦39.2¦51.4¦63.8¦74.2¦79.9¦82.2¦83.3¦83.3¦83.3¦83¦83¦83¦83¦83¦83¦83¦83¦0¦0¦0¦0¦0
117 | Endurance E4660 85kW 23.5m | E4660 | 85.8 |  |  | 23 | 23.5 | No | No | N/A |  |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2.3¦12¦22.8¦37.5¦51.9¦61.7¦71.5¦77.4¦82.3¦84.2¦85.4¦85.6¦84.2¦85.4¦85.8¦85¦85¦85¦85¦85¦85¦85¦0¦0¦0¦0¦0
118 | Northern Power 100-24 | NPS 100-24 | 95.5 | 100 | 90 | 24 | 24 | No | Past | 2011-03-11 | DNV |  |  | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0.9¦5¦11.7¦22.2¦35.5¦49.9¦63.4¦74.7¦83.5¦89.7¦93.7¦95.5¦95.2¦92.5¦87.7¦81.1¦73.8¦67.3¦62.4¦57.7¦54¦50.6¦47.4¦0¦0¦0¦0¦0
119 | Northern Power Northwind 100 | NPS 100-21 | 100 | 100 | 79 | 21 | 21 | No | No | N/A | Manufacturer |  |  | Unknown | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦31¦32¦33¦34¦35¦36¦37¦38¦39¦40 | 0¦0¦0¦0¦3.7¦10.5¦19.0¦29.4¦41.0¦54.3¦66.8¦77.7¦86.4¦92.8¦97.3¦100.0¦100.8¦100.6¦99.8¦99.4¦98.6¦97.8¦97.3¦97.3¦98.0¦99.7¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
120 | NREL 100kW Distributed Commercial Turbine Reference | NREL | 100 |  |  | 13.8 |  | No | No | N/A |  |  | I think this rotor diameter value is actually rotor radius. | unknown | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25 | 0¦0¦0¦3.50595¦8.3104¦16.23125¦28.0476¦44.53855¦66.4832¦94.66065¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100¦100
121 |  | XANT M-21 |  | 100 | 97 |  | 21 | Yes | Yes | unknown | TUV SUD |  | Suggested new turbine to add.
122 |  | Bergey Excel 15 |  | 15 | 15.6 |  | 9.6 | Yes | Yes | 2020-12-04 | SWCC |  | Suggested new turbine to add.
123 |  | Hi VAWT DS3000 |  | 3 | 1.4 |  | 3.66 | Yes | Yes | 2020-06-01 | SWCC |  | Suggested new turbine to add.
124 |  | Bestwind 30 |  | 30 | 27.2 |  | 13.1 | unknown | Yes | 2020-02-01 | SWCC |  | Suggested new turbine to add. No known US sales.
125 |  | Ghrepower FD21-50 |  | 50 | 61.2 |  | 21.5 | Yes | Yes | 2020-05-01 | SWCC |  | Suggested new turbine to add. No known US sales; mainly sold to Japan.
| Electriawind Garbi 150/28 28m 150kw | Electriawind | 150 |  |  | 28 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦5¦10¦19¦34¦55¦80¦108¦150¦150¦150¦150¦150¦150¦150¦150¦150¦150¦150¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Electriawind Garbi 200/28 28m 200kW | Electriawind | 200 |  |  | 28 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦5¦10¦20¦35¦55¦82¦116¦157¦200¦200¦200¦200¦200¦200¦200¦200¦200¦200¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V27-225kw | Vestas | 225 |  |  | 27 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦5¦17¦33¦55¦83¦115¦149¦181¦206¦219¦224¦225¦225¦225¦225¦225¦225¦225¦225¦225¦225¦225¦0¦0¦0¦0¦0
| Endurance X29 225kW 29.1m | Endurance | 229 |  |  | 29 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦10.1¦29.7¦55¦86¦118¦144¦171¦191¦207¦219¦225¦228¦229¦227¦225¦222¦219¦216¦214¦212¦212¦0¦0¦0¦0¦0
| Endurance X33 225kW 33.1m | Endurance | 230 |  |  | 33 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦2.9¦19¦43¦72¦104¦134¦161¦183¦199¦210¦218¦223¦227¦228¦226¦226¦226¦224¦226¦228¦230¦230¦0¦0¦0¦0¦0
| Endurance X30 225kW 30.1 m | Endurance | 233.8 |  |  | 30 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦2.7¦25.6¦55.6¦90.4¦123.1¦159.1¦185.8¦203.8¦216.9¦224.5¦230¦232.7¦233.8¦231.6¦228.4¦223.5¦221¦220¦218¦218¦218¦0¦0¦0¦0¦0
| EWT Directwind 54m 250kW | EWT | 250 |  |  | 54 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦11.3¦39.3¦78.5¦139¦215¦244¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦0¦0¦0¦0¦0
| NREL 250kW Distributed Midsize Turbine Reference | NREL | 250 |  |  | 21.9 | [7 empty] | unknown | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25 | 0¦0¦0¦8.764875¦20.776¦40.578125¦70.119¦111.346375¦166.208¦236.651625¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250
| Wind Energy Solutions WES30 30m 250kw | Wind | 250 |  |  | 30 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦1¦4.4¦14.9¦29.3¦56.3¦77.2¦116¦145¦179¦222¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦250¦0¦0¦0¦0¦0
| Vergnet GEV MP C 30m 275kW | Vergnet | 275 |  |  | 30 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦3¦14¦29¦53¦82¦116¦155¦197¦244¦272¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦0¦0¦0¦0¦0
| Vergnet GEV MP C 32m 275kW | Vergnet | 275 |  |  | 32 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦3¦17.9¦36.5¦58.4¦98.1¦141.1¦188.7¦242.8¦271.7¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦0¦0¦0¦0¦0
| Vergnet GEV MP R 30m 275kW | Vergnet | 275 |  |  | 30 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦3¦14¦29¦53¦82¦116¦155¦197¦244¦272¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦0¦0¦0¦0¦0
| Vergnet GEV MP R 32m 275kW | Vergnet | 275 |  |  | 32 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦3¦17.9¦36.5¦58.4¦98.1¦141.1¦188.7¦242.8¦271.7¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦275¦0¦0¦0¦0¦0
| Enercon E33 33.4m 330kw | Enercon | 335 |  |  | 33 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦5¦13.7¦30¦55¦92¦138¦196¦250¦292¦320¦335¦335¦335¦335¦335¦335¦335¦335¦335¦335¦335¦335¦335¦0¦0¦0¦0¦0
| Enercon E40/5.40 40.3m 550kw | Enercon | 500 |  |  | 40 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦4.37¦18.87¦40.39¦69.36¦112.19¦165.38¦236.89¦328¦396.64¦465.12¦495.95¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦0¦0¦0¦0¦0
| EWT Directwind 52 500kW | EWT | 500 |  |  | 52 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦7¦30¦69¦124¦201¦308¦439¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦0¦0¦0¦0¦0
| EWT Directwind 54 500kW | EWT | 500 |  |  | 54 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦12¦40¦80¦142¦229¦354¦452¦482¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦0¦0¦0¦0¦0
| PowerWind 56-500 56m 500kW | PowerWind | 500 |  |  | 56 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦32¦71¦134¦214¦310¦439¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦0¦0¦0¦0¦0
| Vestas V39-500kw | Vestas | 500 |  |  | 39 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦23¦61¦104¦162¦233¦309¦380¦436¦476¦494¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦500¦0¦0¦0¦0¦0
| Zond Z-40 | Zond | 550 |  |  | 40 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦1.67¦3.42¦10.58¦19.55¦26.72¦32.07¦37.43¦42.79¦55.38¦66.16¦82.35¦94.94¦111.14¦123.73¦136.31¦150.71¦165.1¦177.68¦192.08¦208.28¦224.48¦246.1¦258.69¦273.08¦291.09¦310.91¦341.56¦364.99¦384.81¦395.58¦404.56¦420.76¦442.38¦460.39¦478.39¦487.37¦503.56¦525.19¦537.77¦548.55¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦550¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N43-600 | Nordex | 600 |  |  | 43 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦1.56¦5.46¦9.36¦13.26¦17.16¦24.0325¦30.905¦37.7775¦44.65¦51.4925¦58.335¦65.1775¦72.02¦84.9425¦97.865¦110.7875¦123.71¦141.845¦159.98¦178.115¦196.25¦216.3875¦236.525¦256.6625¦276.8¦298.5075¦320.215¦341.9225¦363.63¦383.7925¦403.955¦424.1175¦444.28¦466.605¦488.93¦511.255¦533.58¦546.1225¦558.665¦571.2075¦583.75¦592.4825¦601.215¦609.9475¦618.68¦618.8825¦619.085¦619.2875¦619.49¦618.8975¦618.305¦617.7125¦617.12¦608.11¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦599.1¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Suzlon S52 600 | Suzlon | 600 |  |  | 52 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦1¦9.25¦17.5¦25.75¦34¦49.5¦65¦80.5¦96¦115.25¦134.5¦153.75¦173¦197¦221¦245¦269¦294.75¦320.5¦346.25¦372¦396.75¦421.5¦446.25¦471¦489.75¦508.5¦527.25¦546¦555.5¦565¦574.5¦584¦588¦592¦596¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Tacke T600-48 | Tacke | 600 |  |  | 48 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦22.5¦28.875¦35.25¦41.625¦48¦57.55¦67.1¦76.65¦86.2¦99.175¦112.15¦125.125¦138.1¦156.025¦173.95¦191.875¦209.8¦228.85¦247.9¦266.95¦286¦306.35¦326.7¦347.05¦367.4¦387.95¦408.5¦429.05¦449.6¦468.475¦487.35¦506.225¦525.1¦534.9¦544.7¦554.5¦564.3¦573.1¦581.9¦590.7¦599.5¦601.95¦604.4¦606.85¦609.3¦611.025¦612.75¦614.475¦616.2¦614.725¦613.25¦611.775¦610.3¦607.85¦605.4¦602.95¦600.5¦597.8¦595.1¦592.4¦589.7¦592.65¦595.6¦598.55¦601.5¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Tacke TW 600 (Old) | Tacke | 600 |  |  | 46 | [7 empty] | unknown | 0.00¦2.95¦3.41¦3.76¦4.28¦4.76¦5.20¦5.71¦6.04¦6.38¦6.79¦7.17¦7.50¦7.84¦8.17¦8.55¦8.86¦9.19¦9.58¦10.04¦10.47¦10.96¦11.52¦12.04¦12.55¦13.24¦14.11¦14.67¦15.21¦18.80¦19.13¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30¦35¦40.00 | 0.00¦0.00¦4.61¦13.83¦27.65¦41.88¦55.31¦73.74¦82.96¦103.70¦129.05¦156.70¦179.75¦207.40¦230.45¦262.71¦290.36¦315.71¦347.98¦382.54¦419.42¦453.98¦497.77¦532.33¦564.60¦592.25¦617.60¦626.82¦629.12¦622.21¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00¦0.00
| Tacke TW-600e | Tacke | 600 |  |  | 46 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦12.8¦12.8¦16.46¦20.12¦23.78¦31.1¦38.41¦49.39¦56.71¦64.02¦75¦85.98¦100.6¦111.58¦137.2¦155.49¦173.78¦188.41¦210.37¦232.32¦246.95¦279.88¦312.8¦334.76¦367.68¦393.29¦411.58¦437.2¦462.8¦477.44¦499.39¦517.68¦532.32¦546.95¦557.93¦568.9¦579.88¦587.2¦600¦600¦605.49¦609.15¦609.15¦609.15¦612.8¦612.8¦612.8¦612.8¦616.46¦616.46¦616.46¦616.46¦616.46¦616.46¦616.46¦620.12¦620.12¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦623.78¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦627.44¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V42-600 | Vestas | 600 |  |  | 42 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦21.5¦32.425¦43.35¦54.275¦65.2¦78.9¦92.6¦106.3¦120¦137¦154¦171¦188¦208¦228¦248¦268¦290¦312¦334¦356¦377¦398¦419¦440¦457.5¦475¦492.5¦510¦521.5¦533¦544.5¦556¦562.5¦569¦575.5¦582¦585¦588¦591¦594¦595¦596¦597¦598¦598.5¦599¦599.5¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V44-600 | Vestas | 600 |  |  | 44 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦30.4¦42.125¦53.85¦65.575¦77.3¦91.725¦106.15¦120.575¦135¦152.75¦170.5¦188.25¦206¦226.25¦246.5¦266.75¦287¦308¦329¦350¦371¦390.75¦410.5¦430.25¦450¦466¦482¦498¦514¦525¦536¦547¦558¦564¦570¦576¦582¦585¦588¦591¦594¦595¦596¦597¦598¦598.5¦599¦599.5¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦600¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V47 660kW | Vestas | 600 |  |  | 47 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦17.9¦68¦130¦192¦263¦370¦445¦513¦554¦582¦595¦598¦600¦600¦600¦600¦600¦600¦600¦600¦600¦0¦0¦0¦0¦0
| Bonus MkIV 44m 600kw | Bonus | 609 |  |  | 44 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦23¦48¦80¦123¦177¦247¦341¦431¦497¦551¦583¦603¦609¦608¦595¦577¦549¦525¦512¦497¦478¦460¦0¦0¦0¦0¦0
| Vestas V47 660 | Vestas | 660 |  |  | 47 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦3.27¦6.89¦13.13¦22.4¦30.15¦43.96¦56.26¦67.01¦82.34¦94¦106.94¦122.27¦139.11¦160.47¦178.83¦200.22¦221.6¦243¦265.9¦284.23¦308.65¦331.56¦355.98¦378.88¦401.79¦421.63¦443.02¦465.92¦488.83¦508.7¦527.06¦540.85¦556.17¦569.99¦583.8¦596.1¦606.85¦616.12¦626.91¦636.17¦642.41¦651.68¦656.37¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦660¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| NEG Micon multi-power 44-750 | NEG | 750 |  |  | 44 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦9.11¦9.17¦16.89¦24.6¦32.34¦40.06¦51.6¦63.12¦74.66¦90.02¦105.38¦120.73¦136.09¦151.43¦170.6¦189.78¦212.77¦235.76¦254.92¦274.09¦297.08¦316.25¦339.25¦362.24¦381.39¦400.56¦423.56¦450.37¦469.54¦484.88¦511.69¦534.68¦553.85¦576.83¦592.18¦615.17¦634.35¦657.34¦676.51¦691.85¦707.21¦722.56¦730.29¦738.01¦738.1¦745.81¦749.71¦749.8¦749.89¦749.98¦750.07¦750.16¦750.23¦746.51¦746.58¦742.87¦739.14¦735.41¦731.68¦727.94¦724.21¦720.48¦716.76¦713.03¦705.48¦705.56¦705.65¦705.73¦705.81¦705.91¦706¦706.09¦706.18¦706.25¦710.16¦710.25¦710.34¦710.43¦710.52¦710.6¦710.68¦710.77¦710.85¦710.95¦711.03¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| NEG Micon multi-power 48-750 | NEG | 750 |  |  | 48 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦9.11¦16.75¦19.69¦28.37¦34.17¦42.85¦54.41¦65.96¦80.39¦97.7¦115¦135.17¦155.34¦184.14¦207.19¦227.35¦250.41¦282.08¦308¦333.92¦359.83¦385.76¦414.56¦440.49¦460.66¦483.71¦518.25¦538.43¦552.85¦573.03¦593.2¦610.5¦627.8¦642.23¦656.66¦671.09¦685.52¦697.07¦705.75¦717.31¦723.11¦731.79¦737.6¦740.53¦749.21¦749.27¦752.2¦752.26¦755.2¦755.26¦755.32¦755.38¦755.44¦752.63¦752.69¦749.87¦749.93¦744.24¦741.43¦738.62¦735.8¦730.11¦727.3¦721.62¦715.93¦710.24¦707.43¦701.74¦698.93¦698.99¦696.17¦696.23¦693.42¦693.48¦693.54¦693.58¦693.65¦693.72¦693.78¦696.71¦696.77¦699.71¦699.76¦696.95¦696.95¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| WindEnergyLebanon 750kW 54m | WindEnergyLebanon | 750 |  |  | 54 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦19¦52¦104¦173¦278¦396¦548¦686¦745¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦0¦0¦0¦0¦0
| WindEnergyLebanon 750kW 57m | WindEnergyLebanon | 750 |  |  | 57 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦26¦62¦123¦204¦316¦451¦622¦728¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦0¦0¦0¦0¦0
| Zond Z-50¦750 | Zond | 750 |  |  | 50 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦8.29¦15.09¦28¦40.54¦53.39¦66.24¦78.83¦97.47¦116.11¦128.71¦147.34¦171.77¦190.16¦214.58¦244.81¦263.19¦293.41¦323.63¦353.58¦383.81¦419.81¦455.83¦480.01¦510.22¦540¦564.62¦600.63¦625.06¦666.85¦691.03¦721.25¦739.89¦746.69¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦750¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| WindEnergyLebanon 750kW 50m | WindEnergyLebanon | 752.663 |  |  | 50 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦11.834¦42.604¦87.574¦151.479¦234.32¦336.095¦466.272¦624.852¦726.627¦747.929¦750.296¦747.929¦752.663¦752.663¦750.296¦752.663¦750.296¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Gamesa G52 800 | Gamesa | 800 |  |  | 52 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦16.6¦24.875¦33.15¦41.425¦49.7¦63.4¦77.1¦90.8¦104.5¦125.725¦146.95¦168.175¦189.4¦213.45¦237.5¦261.55¦285.6¦316.375¦347.15¦377.925¦408.7¦440.025¦471.35¦502.675¦534¦566¦598¦630¦662¦684.25¦706.5¦728.75¦751¦760.25¦769.5¦778.75¦788¦789.5¦791¦792.5¦794¦795.5¦797¦798.5¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦800¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Enercon E48 48m 800kw | Enercon | 810 |  |  | 48 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦2¦12¦32¦66¦120¦191¦284¦405¦555¦671¦750¦790¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦0¦0¦0¦0¦0
| Enercon E53 52.9m 800kw | Enercon | 810 |  |  | 52 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦2¦14¦38¦77¦141¦228¦336¦480¦645¦744¦780¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦810¦0¦0¦0¦0¦0
| Gamesa G52 850 | Gamesa | 850 |  |  | 52 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦27.9¦37.225¦46.55¦55.875¦65.2¦79.675¦94.15¦108.625¦123.1¦143.075¦163.05¦183.025¦203¦229¦255¦281¦307¦339.075¦371.15¦403.225¦435.3¦467.6¦499.9¦532.2¦564.5¦594.525¦624.55¦654.575¦684.6¦708.425¦732.25¦756.075¦779.9¦795.075¦810.25¦825.425¦840.6¦842.45¦844.3¦846.15¦848¦848.25¦848.5¦848.75¦849¦849.25¦849.5¦849.75¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Gamesa G58 -850kw | Gamesa | 850 |  |  | 58 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦9.7¦31.2¦78.4¦148.2¦242.7¦368.8¦525.3¦695¦796.6¦835.9¦846.8¦849.3¦849.9¦850¦850¦850¦850¦850¦850¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V52-850 | Vestas | 850 |  |  | 52 | [7 empty] | I¦II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦9.11¦13.19¦22.48¦28.74¦37.99¦47.29¦59.6¦65.83¦81.18¦96.54¦105.83¦115.08¦130.43¦148.81¦170.19¦191.6¦206.96¦231.35¦252.77¦274.19¦301.66¦320.01¦344.45¦371.92¦396.33¦426.83¦454.31¦481.74¦515.28¦536.69¦567.19¦591.6¦609.98¦634.43¦652.77¦677.21¦698.63¦713.94¦741.41¦762.83¦778.18¦790.46¦802.79¦809.05¦818.3¦827.58¦836.88¦846.14¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦850¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Americas Wind Energy 52-900 | Americas | 900 |  |  | 52 | [7 empty] | II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦1¦2.75¦4.0625¦5.375¦8¦13.75¦18.0625¦22.375¦31¦40.5¦47.625¦54.75¦69¦82.75¦93.0625¦103.375¦124¦142.75¦156.8125¦170.875¦199¦223.5¦241.875¦260.25¦297¦327¦349.5¦372¦417¦450¦474.75¦499.5¦549¦591¦622.5¦654¦717¦731.5¦742.375¦753.25¦775¦787.5¦796.875¦806.25¦825¦837.5¦846.875¦856.25¦875¦881.25¦885.9375¦890.625¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Americas Wind Energy 54-900 | Americas | 900 |  |  | 54 | [7 empty] | III | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦1¦3¦4.5¦6¦9¦15¦19.5¦24¦33¦43¦50.5¦58¦73¦88¦99.25¦110.5¦133¦153¦168¦183¦213¦239.25¦258.9375¦278.625¦318¦350.25¦374.4375¦398.625¦447¦482¦508.25¦534.5¦587¦632¦665.75¦699.5¦767¦782.5¦794.125¦805.75¦829¦842.5¦852.625¦862.75¦883¦887.25¦890.4375¦893.625¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦900¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| NEG Micon 52 900 | NEG | 900 |  |  | 52 | [7 empty] | I | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦16.02¦26.1¦36.19¦46.26¦58.35¦68.44¦80.53¦90.6¦104.71¦120.81¦136.92¦155.03¦173.15¦193.27¦213.39¦235.52¦257.66¦279.79¦301.91¦326.05¦350.19¦374.33¦400.47¦428.63¦464.81¦501¦533.17¦563.34¦591.49¦619.64¦645.79¦671.93¦694.07¦718.2¦740.33¦760.46¦778.56¦792.67¦814.8¦828.9¦840.99¦853.08¦865.17¦873.24¦881.32¦887.38¦895.45¦899.51¦901.56¦901.6¦901.65¦899.68¦895.71¦889.72¦883.74¦877.76¦871.78¦865.79¦861.81¦855.83¦851.85¦847.89¦841.91¦837.93¦833.96¦829.98¦828.02¦824.04¦822.08¦820.11¦812.12¦810.16¦806.18¦802.21¦800.24¦798.28¦796.31¦794.34¦792.38¦790.41¦788.45¦786.48¦784.51¦784.55¦782.58¦782.63¦780.65¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Enercon E44 44m 900kw | Enercon | 910 |  |  | 44 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦1.4¦8¦24.5¦53¦96¦156¦238¦340¦466¦600¦710¦790¦850¦880¦905¦910¦910¦910¦910¦910¦910¦910¦910¦910¦0¦0¦0¦0¦0
| Suzlon S64-950 | Suzlon | 950 |  |  | 64 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦16¦21.25¦26.5¦31.75¦37¦52.75¦68.5¦84.25¦100¦120.25¦140.5¦160.75¦181¦207.5¦234¦260.5¦287¦328.25¦369.5¦410.75¦452¦500.25¦548.5¦596.75¦645¦699¦753¦807¦861¦883.25¦905.5¦927.75¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦950¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Mitsubishi MWT 1000 | Mitsubishi | 1000 |  |  | 57 | [7 empty] | I | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦1.03¦5.17¦11.35¦19.63¦34.09¦46.49¦69.21¦85.74¦104.34¦127.07¦145.66¦174.58¦201.45¦228.31¦265.5¦292.35¦327.48¦354.34¦381.2¦418.39¦445.25¦480.37¦507.23¦542.35¦589.88¦627.07¦674.58¦707.64¦751.03¦782.02¦813.02¦854.34¦881.2¦916.32¦941.12¦961.78¦976.24¦989¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Mitsubishi MWT 1000A | Mitsubishi | 1000 |  |  | 61.4 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0.78¦14.75¦27.17¦39.6¦53.56¦69.1¦90.83¦107.92¦131.21¦156.06¦182.45¦218.17¦246.12¦275.62¦305.12¦334.63¦365.68¦407.6¦444.88¦482.14¦519.41¦555.12¦592.39¦638.98¦676.24¦711.96¦749.22¦784.94¦826.85¦859.47¦887.42¦913.81¦937.11¦958.85¦975.93¦985.25¦989.91¦994.56¦1000¦1000¦1000¦1000¦999.22¦999.22¦999.22¦999.22¦999.22¦999.22¦999.22¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vergnet GEV HP(104.4dba)_62m_1000kw | Vergnet | 1000 |  |  | 62 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦7¦43¦95¦168¦269¦399¦560¦731¦859¦929¦969¦990¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦0¦0¦0¦0¦0
| Nordic 1000 54m 1000kW | Nordic | 1011.4 |  |  | 54 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦32¦103.8¦198¦312.1¦437.8¦561.7¦681.3¦801.1¦892.2¦956.9¦994¦1010¦1011.4¦1005.8¦996.6¦983.9¦973.4¦966.3¦962.4¦958.4¦954.5¦0¦0¦0¦0¦0
| AAER Systems AAER A-1000/S 54m 1100kw | AAER | 1037 |  |  | 54 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦24¦64¦111¦197¦314¦454¦582¦686¦783¦891¦966¦1010¦1037¦1030¦1035¦1032¦1009¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| WindEnergyLebanon 1MW 54.4m | WindEnergyLebanon | 1048 |  |  | 54 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦30¦73¦138¦231¦349¦481¦610¦742¦877¦973¦1032¦1048¦1035¦1008¦1000¦1000¦1000¦1000¦1000¦1000¦1000¦0¦0¦0¦0¦0
| Suzlon S64-1250 | Suzlon | 1250 |  |  | 64 | [7 empty] | II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦8.75¦17.5¦35¦48.5¦62¦75.5¦89¦103.75¦118.5¦133.25¦148¦179.75¦211.5¦243.25¦275¦317.75¦360.5¦403.25¦446¦489.75¦533.5¦577.25¦621¦668.5¦716¦763.5¦811¦855.75¦900.5¦945.25¦990¦1024.25¦1058.5¦1092.75¦1127¦1144.75¦1162.5¦1180.25¦1198¦1211¦1224¦1237¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Suzlon S66_1250_66m_1250kw | Suzlon | 1250 |  |  | 66 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦5¦35¦93¦151¦285¦454¦639¦832¦1008¦1152¦1241¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦1250¦0¦0¦0¦0¦0
| Bonus 1300 | Bonus | 1300 |  |  | 62 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦32¦46.5¦57.375¦68.25¦90¦110.5¦125.875¦141.25¦172¦200.5¦221.875¦243.25¦286¦324.75¦353.8125¦382.875¦441¦487¦521.5¦556¦625¦673.75¦710.3125¦746.875¦820¦866.5¦901.375¦936.25¦1006¦1042.75¦1070.3125¦1097.875¦1153¦1175¦1191.5¦1208¦1241¦1250.75¦1258.0625¦1265.375¦1280¦1283.5¦1286.125¦1288.75¦1294¦1295¦1295.75¦1296.5¦1298¦1298.5¦1298.875¦1299.25¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦1300¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N60-1300 | Nordex | 1300 |  |  | 60 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦7.25¦14.5¦21.75¦29¦40¦51¦62¦73¦87.5¦102¦116.5¦131¦158.5¦186¦213.5¦241¦274.75¦308.5¦342.25¦376¦416¦456¦496¦536¦578¦620¦662¦704¦745.75¦787.5¦829.25¦871¦907.25¦943.5¦979.75¦1016¦1043¦1070¦1097¦1124¦1154.75¦1185.5¦1216.25¦1247¦1260.5¦1274¦1287.5¦1301¦1311.75¦1322.5¦1333.25¦1344¦1349¦1354¦1359¦1364¦1353.5¦1343¦1332.5¦1322¦1321.25¦1320.5¦1319.75¦1319¦1317.75¦1316.5¦1315.25¦1314¦1313.5¦1313¦1312.5¦1312¦1310.75¦1309.5¦1308.25¦1307¦1305¦1303¦1301¦1299¦1297.25¦1295.5¦1293.75¦1292¦1292¦1292¦1292¦1292¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| AAER A-1500_70 | AAER | 1500 |  |  | 70 | [7 empty] | I¦II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦8.5¦17¦25.5¦34¦50.25¦66.5¦82.75¦99¦122.5¦146¦169.5¦193¦227¦261¦295¦329¦373.5¦418¦462.5¦507¦565¦623¦681¦739¦809.5¦880¦950.5¦1021¦1099.25¦1177.5¦1255.75¦1334¦1375.5¦1417¦1458.5¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| AAER A-1500_77 | AAER | 1500 |  |  | 77 | [7 empty] | II¦III | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦10¦20¦30¦40¦59.5¦79¦98.5¦118¦146.5¦175¦203.5¦232¦272.75¦313.5¦354.25¦395¦448.25¦501.5¦554.75¦608¦677.75¦747.5¦817.25¦887¦971.5¦1056¦1140.5¦1225¦1281.25¦1337.5¦1393.75¦1450¦1462.5¦1475¦1487.5¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Composite IEC Class I | Composite | 1500 |  |  | 90 | [7 empty] | I | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦28.5¦46.875¦65.25¦83.625¦102¦129¦156¦183¦210¦246.375¦282.75¦319.125¦355.5¦403.875¦452.25¦500.625¦549¦607.875¦666.75¦725.625¦784.5¦851.625¦918.75¦985.875¦1053¦1110.75¦1168.5¦1226.25¦1284¦1321.5¦1359¦1396.5¦1434¦1445.625¦1457.25¦1468.875¦1480.5¦1483.125¦1485.75¦1488.375¦1491¦1492.5¦1494¦1495.5¦1497¦1497.375¦1497.75¦1498.125¦1498.5¦1498.875¦1499.15625¦1499.3671875¦1499.525390625¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Composite IEC Class II | Composite | 1500 |  |  | 90 | [7 empty] | II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦42¦64.5¦87¦109.5¦132¦164.25¦196.5¦228.75¦261¦303.375¦345.75¦388.125¦430.5¦485.625¦540.75¦595.875¦651¦715.875¦780.75¦845.625¦910.5¦974.25¦1038¦1101.75¦1165.5¦1213.5¦1261.5¦1309.5¦1357.5¦1382.625¦1407.75¦1432.875¦1458¦1465.875¦1473.75¦1481.625¦1489.5¦1491.375¦1493.25¦1495.125¦1497¦1497.75¦1498.5¦1499.25¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Composite IEC Class III | Composite | 1500 |  |  | 90 | [7 empty] | III | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦9¦22.125¦35.25¦48.375¦61.5¦84.375¦107.25¦130.125¦153¦185.625¦218.25¦250.875¦283.5¦329.25¦375¦420.75¦466.5¦526.875¦587.25¦647.625¦708¦779.625¦851.25¦922.875¦994.5¦1060.125¦1125.75¦1191.375¦1257¦1297.5¦1338¦1378.5¦1419¦1434.375¦1449.75¦1465.125¦1480.5¦1484.625¦1488.75¦1492.875¦1497¦1497.375¦1497.75¦1498.125¦1498.5¦1498.875¦1499.25¦1499.625¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Fuhrlander FL 1500_70 | Fuhrlander | 1500 |  |  | 70 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦10¦21.91¦29.8¦37.69¦45.58¦66.7¦87.83¦108.95¦124.77¦148.54¦180.24¦214.58¦241¦277.99¦312.34¦336.11¦383.68¦433.9¦484.12¦542.28¦595.15¦655.95¦722.04¦788.14¦859.52¦928.26¦1000¦1070¦1150¦1220¦1290¦1360¦1410¦1440¦1460¦1490¦1500¦1500¦1500¦1510¦1510¦1510¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1520¦1510¦1510¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Fuhrlander FL 1500_77 | Fuhrlander | 1500 |  |  | 77 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦10¦21.91¦29.8¦37.69¦45.58¦66.7¦90.47¦119.53¦143.29¦169.7¦185.54¦214.58¦241¦277.99¦309.7¦336.11¦383.68¦433.9¦484.12¦542.28¦611.02¦706.21¦793.47¦888.66¦965.34¦1010¦1050¦1090¦1150¦1240¦1320¦1420¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| GE 1.5 xle | GE | 1500 |  |  | 82.5 | [7 empty] | IIIb | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦13.98¦45.74¦114.19¦145.94¦177.69¦211.89¦248.54¦285.18¦324.28¦363.37¦409.81¦463.58¦522.24¦588.24¦659.14¦727.58¦800.94¦876.73¦947.62¦1060¦1130¦1200¦1260¦1310¦1350¦1390¦1420¦1450¦1470¦1490¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| GE 1.5s | GE | 1500 |  |  | 70 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦36¦51¦66¦85¦104¦127¦150¦177.5¦205¦237¦269¦306.5¦344¦386¦428¦478¦528¦586¦644¦709¦774¦850.25¦926.5¦1002.75¦1079¦1145¦1211¦1276.5¦1342¦1371.5¦1401¦1430.5¦1460¦1468.5¦1477¦1485.5¦1494¦1497¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| GE 1.5sle | GE | 1500 |  |  | 77 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦21.32¦33.51¦45.69¦65.21¦79.83¦104.25¦128.66¦157.97¦187.27¦216.58¦250.78¦292.32¦333.85¦375.4¦426.72¦475.6¦534.27¦597.81¦656.49¦724.94¦798.29¦871.63¦940.08¦1010¦1060¦1130¦1190¦1240¦1290¦1330¦1370¦1390¦1410¦1430¦1440¦1460¦1470¦1475¦1480¦1485¦1490¦1495¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Leitwind LTW77m 1.5MW | Leitwind | 1500 |  |  | 77 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦61¦135¦248¦406¦619¦877¦1158¦1435¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0
| Leitwind LTW80 1.5MW | Leitwind | 1500 |  |  | 80 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦77¦184¦330¦527¦761¦993¦1268¦1462¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0
| NEG Micon 72C 1500 | NEG | 1500 |  |  | 72 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦74¦106¦138¦170¦202¦240.5¦279¦317.5¦356¦411¦466¦521¦576¦634¦692¦750¦808¦870.5¦933¦995.5¦1058¦1114.75¦1171.5¦1228.25¦1285¦1320.25¦1355.5¦1390.75¦1426¦1432.25¦1438.5¦1444.75¦1451¦1459¦1467¦1475¦1483¦1487.25¦1491.5¦1495.75¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N70 - 1.5MW | Nordex | 1500 |  |  | 70 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦24¦87¦190¦329¦520¦750¦1016¦1284¦1426¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0
| Nordex S70 1500kw | Nordex | 1500 |  |  | 70 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦24¦87¦190¦329¦531¦736¦1016¦1284¦1426¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0
| Nordex S77 1500kw | Nordex | 1500 |  |  | 77 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦44¦131¦244¦400¦600¦854¦1111¦1331¦1476¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0
| Suzlon S82 1.5 | Suzlon | 1500 |  |  | 82 | [7 empty] | IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦1¦25.5¦50¦74.5¦99¦140¦181¦222¦263¦313.75¦364.5¦415.25¦466¦526.75¦587.5¦648.25¦709¦775.25¦841.5¦907.75¦974¦1035.25¦1096.5¦1157.75¦1219¦1259.75¦1300.5¦1341.25¦1382¦1396¦1410¦1424¦1438¦1446.75¦1455.5¦1464.25¦1473¦1479.75¦1486.5¦1493.25¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vensys 70 1.5MW | Vensys | 1500 |  |  | 70 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦52.5¦120¦214.8¦344.2¦521.1¦740.5¦989.8¦1232.8¦1410.7¦1479.1¦1497.5¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0
| Vensys 77m 1500kW | Vensys | 1500 |  |  | 77 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦70.8¦147.7¦262.7¦420.3¦633.7¦892.5¦1161.5¦1372.7¦1468.3¦1495.6¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0
| Vensys 82m 1500kW | Vensys | 1500 |  |  | 82 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦85.8¦175.1¦311¦496.8¦746.8¦1040.6¦1309.4¦1461.6¦1491.2¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦1500¦0¦0¦0¦0¦0¦0¦0¦0
| General Electric GE 1.6mW 100m | General | 1600 |  |  | 100 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦38¦154¦405¦693¦986¦1323¦1506¦1578¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦1600¦0¦0¦0¦0¦0
| NEG Micon 82 1650 | NEG | 1650 |  |  | 82 | [7 empty] | III | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦28¦57¦86¦115¦144¦185.25¦226.5¦267.75¦309¦359.5¦410¦460.5¦511¦572.75¦634.5¦696.25¦758¦822.75¦887.5¦952.25¦1017¦1077.25¦1137.5¦1197.75¦1258¦1319.5¦1381¦1442.5¦1504¦1537.25¦1570.5¦1603.75¦1637¦1639.75¦1642.5¦1645.25¦1648¦1648.5¦1649¦1649.5¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V66-1650 | Vestas | 1650 |  |  | 66 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦7.5¦22.325¦37.15¦51.975¦66.8¦86.1¦105.4¦124.7¦144¦170.35¦196.7¦223.05¦249.4¦284.1¦318.8¦353.5¦388.2¦431.1¦474¦516.9¦559.8¦606.8¦653.8¦700.8¦747.8¦794.3¦840.8¦887.3¦933.8¦977.25¦1020.7¦1064.15¦1107.6¦1147.85¦1188.1¦1228.35¦1268.6¦1304.95¦1341.3¦1377.65¦1414¦1442.9¦1471.8¦1500.7¦1529.6¦1547.8¦1566¦1584.2¦1602.4¦1610.8¦1619.2¦1627.6¦1636¦1638.5¦1641¦1643.5¦1646¦1647¦1648¦1649¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V82-1.65 | Vestas | 1650 |  |  | 82 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦18.92¦46.54¦73.81¦108.85¦147.79¦194.49¦237.3¦287.89¦338.47¦389.05¦451.29¦505.76¦567.99¦618.56¦680.81¦739.16¦797.51¦863.62¦921.97¦984.21¦1040¦1100¦1160¦1210¦1260¦1310¦1360¦1400¦1440¦1470¦1500¦1530¦1550¦1560¦1580¦1600¦1610¦1620¦1630¦1640¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦1650¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| AAER Systems AAER A1650 77m 1650kW Class IIa | AAER | 1651 |  |  | 77 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦57¦141¦258¦422¦642¦919¦1237¦1541¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| AAER Systems AAER A1650 82m 1650kW Class IIIa | AAER | 1651 |  |  | 82 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦71¦173¦316¦516¦781¦1117¦1520¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦1651¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Leitwind LTW70 1.7MW | Leitwind | 1700 |  |  | 70 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦58¦120¦213¦344¦519¦742¦1018¦1327¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦1700¦0¦0¦0¦0¦0
| Leitwind LTW80 1.8MW | Leitwind | 1800 |  |  | 80 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦80¦163¦287¦460¦691¦986¦1346¦1749¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1780¦1760¦1740¦1720¦1700¦0¦0¦0¦0¦0
| Vestas V100-1.8 | Vestas | 1800 |  |  | 100 | [7 empty] | IIa¦IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦119.31¦139.91¦181.12¦222.32¦266.95¦308.15¦359.66¦411.16¦469.53¦527.9¦600¦665.24¦747.64¦826.6¦919.31¦1010¦1110¦1200¦1290¦1390¦1460¦1550¦1620¦1690¦1730¦1750¦1770¦1780¦1790¦1790¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V80-1.8 | Vestas | 1800 |  |  | 80 | [7 empty] | I | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦3¦27¦51¦75¦99¦139.25¦179.5¦219.75¦260¦311.25¦362.5¦413.75¦465¦532.5¦600¦667.5¦735¦805¦875¦945¦1015¦1097.5¦1180¦1262.5¦1345¦1418.5¦1492¦1565.5¦1639¦1673¦1707¦1741¦1775¦1780.5¦1786¦1791.5¦1797¦1798.25¦1799.5¦1800.75¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1802¦1801.5¦1801¦1800.5¦1800¦1800¦1800¦1800¦1800¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V90-1.8 | Vestas | 1800 |  |  | 90 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦18.56¦35.39¦52.21¦74.56¦96.88¦124.69¦157.99¦191.29¦241.12¦279.92¦335.2¦368.5¦423.78¦490.05¦556.37¦622.64¦683.41¦755.18¦832.43¦904.2¦992.49¦1080¦1140¦1220¦1310¦1410¦1480¦1570¦1640¦1700¦1750¦1770¦1790¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦1800¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Enercon E66 1870lW | Enercon | 1870 |  |  | 66 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦14¦52¦115¦201¦325¦492¦712¦990¦1300¦1557¦1720¦1825¦1854¦1870¦1870¦1870¦1870¦1870¦1870¦1870¦1870¦1870¦1870¦0¦0¦0¦0¦0
| DeWind D8(8.2) | DeWind | 2000 |  |  | 80 | [7 empty] | I¦II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦3.62666666666667¦7.25333333333333¦10.88¦14.9¦26.75¦34.69¦50.48¦66.27¦85.97¦113.52¦141.07¦180.39¦215.77¦255.09¦298.32¦353.33¦396.56¦459.41¦518.32¦589.01¦655.78¦730.38¦804.99¦883.53¦965.97¦1060¦1150¦1250¦1350¦1440¦1540¦1630¦1700¦1770¦1810¦1860¦1900¦1930¦1950¦1980¦1990¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| EWT Directwind 90m 2mW | EWT | 2000 |  |  | 90 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦87¦199¦372¦596¦892¦1238¦1600¦1926¦1992¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0
| EWT Directwind 96m 2mW Direct Drive | EWT | 2000 |  |  | 96 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦119¦246¦426¦681¦984¦1362¦1753¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0
| Gamesa G114 2.0 MW | Gamesa | 2000 |  |  | 114 | [7 empty] | unknown | 2.0¦3.0¦4.0¦5.0¦6.0¦7.0¦8.0¦9.0¦10.0¦11.0¦12.0¦13.0¦14.0¦15.0¦16.0¦17.0¦18.0¦19.0¦20.0¦21.0¦22.0¦23.0¦24.0¦25.0 | 0¦32¦146¦342¦621¦1008¦1486¦1836¦1965¦1994¦1999¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦1906¦1681¦1455¦1230
| Gamesa G80 2.0MW | Gamesa | 2000 |  |  | 80 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦66.3¦87.725¦109.15¦130.575¦152¦184¦216¦248¦280¦324.25¦368.5¦412.75¦457¦515.25¦573.5¦631.75¦690¦762¦834¦906¦978¦1057.5¦1137¦1216.5¦1296¦1371.5¦1447¦1522.5¦1598¦1653¦1708¦1763¦1818¦1847.25¦1876.5¦1905.75¦1935¦1946.25¦1957.5¦1968.75¦1980¦1983.75¦1987.5¦1991.25¦1995¦1996¦1997¦1998¦1999¦1999.25¦1999.5¦1999.75¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Gamesa G83 -2.0MW | Gamesa | 2000 |  |  | 83 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦65.1¦152.4¦285.2¦470.8¦715.8¦1024.8¦1377.4¦1690.8¦1881.9¦1963.8¦1990.3¦1997.6¦1999.4¦1999.9¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0
| Gamesa G87 2.0 MW | Gamesa | 2000 |  |  | 87 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦78.6¦104.25¦129.9¦155.55¦181.2¦219.75¦258.3¦296.85¦335.4¦389¦442.6¦496.2¦549.8¦620.225¦690.65¦761.075¦831.5¦917.325¦1003.15¦1088.975¦1174.8¦1263.175¦1351.55¦1439.925¦1528.3¦1594.9¦1661.5¦1728.1¦1794.7¦1828.8¦1862.9¦1897¦1931.1¦1943.575¦1956.05¦1968.525¦1981¦1984.575¦1988.15¦1991.725¦1995.3¦1996.2¦1997.1¦1998¦1998.9¦1999.125¦1999.35¦1999.575¦1999.8¦1999.85¦1999.9¦1999.95¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Gamesa G90 2.0 MW | Gamesa | 2000 |  |  | 90 | [7 empty] | IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦21.3¦37.2¦53.1¦69¦84.9¦113¦141.1¦169.2¦197.3¦238.925¦280.55¦322.175¦363.8¦421.575¦479.35¦537.125¦594.9¦671.375¦747.85¦824.325¦900.8¦994.2¦1087.6¦1181¦1274.4¦1364.05¦1453.7¦1543.35¦1633¦1690.5¦1748¦1805.5¦1863¦1887.35¦1911.7¦1936.05¦1960.4¦1967.9¦1975.4¦1982.9¦1990.4¦1992.275¦1994.15¦1996.025¦1997.9¦1998.325¦1998.75¦1999.175¦1999.6¦1999.675¦1999.75¦1999.825¦1999.9¦1999.925¦1999.95¦1999.975¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Gamesa G97 2.0 MW | Gamesa | 2000 |  |  | 97 | [7 empty] | unknown | 2.0¦3.0¦4.0¦5.0¦6.0¦7.0¦8.0¦9.0¦10.0¦11.0¦12.0¦13.0¦14.0¦15.0¦16.0¦17.0¦18.0¦19.0¦20.0¦21.0¦22.0¦23.0¦24.0¦25.0 | 0¦14¦94¦236¦438¦714¦1084¦1508¦1836¦1973¦1992¦1998¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦1676¦1234
| Leitwind LTW70 2MW | Leitwind | 2000 |  |  | 70 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦57¦120¦214¦347¦524¦749¦1012¦1309¦1625¦1900¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0
| NREL 2000kW Distributed Large Turbine Reference | NREL | 2000 |  |  | 55 | [7 empty] | unknown | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25 | 0¦0¦0¦70.119¦166.208¦324.625¦560.952¦890.771¦1329.664¦1893.213¦2000¦2000¦2000¦2000¦2000¦2000 ¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000
| Vestas V100-2.0 | Vestas | 2000 |  |  | 100 | [7 empty] | unknown | 3¦3.0014858¦3.9970284¦5.0074296¦6.0029716¦6.998514¦8.008915¦9.004457¦10¦11.010401¦12.005943¦13.001486¦14.011887¦15.007429¦16.002972¦17.013372¦18.008915¦19.004457¦20.014858¦21.0104¦21.991085 | 0¦12.716763¦99.61465¦258.5742¦464.16183¦718.49713¦1102.1195¦1540.8478¦1879.9614¦1983.8151¦2000.7708¦2000.7708¦2000.7708¦2000.7708¦2000.7708¦2000.7708¦2000.7708¦2000.7708¦2000.7708¦2002.8901¦2000.7708
| Vestas V110-2.0 | Vestas | 2000 |  |  | 110 | [7 empty] | unknown | 2¦2.9999037¦3.994556¦5.003854¦5.998087¦6.9919233¦8.000265¦8.993844¦9.98821¦10.998014¦11.993056¦12.988106¦13.998007¦14.993056¦15.973247¦16.998005¦17.993055¦18.988104¦19.983154 | 0¦27.738222¦142.14922¦315.84906¦550.9531¦900.3979¦1349.3625¦1772.9171¦1969.9076¦1997.5054¦1999.693¦1999.7632¦1999.8345¦1999.9047¦2002.0913¦2000.0463¦2000.1165¦2000.1866¦2000.257
| Vestas V80-2.0 | Vestas | 2000 |  |  | 80 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦58.85¦62.25¦72.48¦89.6¦106.71¦127.26¦154.67¦178.66¦223.26¦264.42¦309.03¦360.5¦411.98¦470.32¦525.24¦597.33¦645.37¦710.58¦768.94¦837.58¦899.38¦968.03¦1030¦1110¦1170¦1240¦1300¦1370¦1420¦1490¦1550¦1610¦1660¦1710¦1750¦1800¦1830¦1860¦1890¦1910¦1930¦1940¦1950¦1960¦1970¦1980¦1985¦1990¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V90-2.0 | Vestas | 2000 |  |  | 90 | [7 empty] | IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦4.595¦9.19¦13.785¦18.38¦29.56¦40.88¦57.7¦80.06¦102.37¦130.18¦157.99¦191.29¦241.12¦279.92¦329.71¦379.49¦429.28¦490.05¦556.37¦617.14¦677.92¦755.18¦826.94¦904.2¦997.99¦1090¦1190¦1260¦1350¦1460¦1560¦1650¦1730¦1800¦1860¦1910¦1950¦1960¦1970¦1980¦1990¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦2000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| AAER Systems AAER A-2000-71 71m 2000kw | AAER | 2001 |  |  | 71 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦60¦169¦298¦470¦721¦1025¦1355¦1660¦1939¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦0¦0¦0¦0¦0
| AAER Systems AAER A-2000-80 80m 2000kw | AAER | 2001 |  |  | 80 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦14¦111¦249¦436¦683¦1006¦1387¦1773¦1974¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| AAER Systems AAER A-2000-84 84m 2000kw | AAER | 2001 |  |  | 84 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦43¦146¦292¦494¦774¦1136¦1567¦1926¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦2001¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Enercon E66 20.7mW | Enercon | 2005 |  |  | 66 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦48¦105¦202¦337¦521¦749¦1021¦1353¦1703¦1852¦2005¦2005¦2005¦2005¦2005¦2005¦2005¦2005¦2005¦2005¦2005¦2005¦0¦0¦0¦0¦0
| Senvion MM100 2mW | Senvion | 2020 |  |  | 100 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦110¦236¦446¦709¦1067¦1488¦1862¦1993¦2020¦2020¦2020¦2020¦2020¦2020¦2020¦2020¦2020¦2020¦2020¦0¦0¦0¦0¦0¦0¦0¦0
| Enercon E82 E2 82m 2000kw | Enercon | 2050 |  |  | 82 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦3¦25¦82¦174¦321¦532¦815¦1180¦1612¦1890¦2000¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦0¦0¦0¦0¦0
| RePower MM 82 | RePower | 2050 |  |  | 82 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦13.48¦18.1¦28.26¦48.48¦63.65¦88.88¦109.08¦139.35¦164.56¦194.81¦225.07¦265.37¦305.68¦345.98¦386.28¦426.56¦466.87¦517.22¦577.63¦633¦683.34¦738.71¦804.13¦869.55¦945.03¦1000¦1080¦1150¦1220¦1300¦1380¦1450¦1510¦1580¦1640¦1700¦1770¦1820¦1870¦1910¦1940¦1980¦2010¦2030¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| RePower MM 92 | RePower | 2050 |  |  | 92 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦4.49333333333333¦8.98666666666667¦13.48¦34.5¦55.19¦75.8¦96.4¦122.03¦152.76¦188.44¦224.11¦259.79¦305.58¦351.31¦386.99¦437.73¦508.66¦554.38¦610.15¦686.09¦741.85¦807.68¦883.54¦969.53¦1050¦1120¦1210¦1310¦1380¦1500¦1590¦1680¦1770¦1860¦1930¦1990¦2030¦2040¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦2050¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Suzlon S88 | Suzlon | 2100 |  |  | 88 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦14¦45¦76¦107¦138¦181.5¦225¦268.5¦312¦370.5¦429¦487.5¦546¦619.5¦693¦766.5¦840¦925¦1010¦1095¦1180¦1268.75¦1357.5¦1446.25¦1535¦1615.25¦1695.5¦1775.75¦1856¦1901.25¦1946.5¦1991.75¦2037¦2049.75¦2062.5¦2075.25¦2088¦2091¦2094¦2097¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦2100¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N90-2300 | Nordex | 2300 |  |  | 90 | [7 empty] | II | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦8.75¦17.5¦26.25¦35¦70¦105¦140¦175¦219.25¦263.5¦307.75¦352¦409¦466¦523¦580¦652.5¦725¦797.5¦870¦961.75¦1053.5¦1145.25¦1237¦1333.5¦1430¦1526.5¦1623¦1720.25¦1817.5¦1914.75¦2012¦2066.5¦2121¦2175.5¦2230¦2247.5¦2265¦2282.5¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Siemens SWT 2.3 MW-93 | Siemens | 2300 |  |  | 93 | [7 empty] | not listed | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦38.515¦77.03¦95.4¦109.39¦123.38¦141.56¦173.08¦213.35¦258¦298.1¦355.89¦418.06¦475.85¦533.47¦608.78¦675.33¦746.26¦808.26¦883.56¦963.26¦1040¦1110¦1200¦1280¦1350¦1440¦1520¦1620¦1690¦1760¦1830¦1890¦1950¦2030¦2090¦2130¦2190¦2230¦2260¦2280¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Siemens SWT-2.3MW-101m | Siemens | 2300 |  |  | 101 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦102¦252¦462¦774¦1163¦1583¦2014¦2254¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦2300¦0¦0¦0¦0¦0
| Siemens SWT-2.3MW-108m | Siemens | 2300 |  |  | 108 | [7 empty] | unknown | 3¦3.0387623¦4.0104685¦5.0265937¦6.0029287¦7.023861¦8.005003¦9.02816¦10.00494¦11.018574¦12.031316¦13.001776¦14.01434¦15.027083¦15.997543¦17.010197¦18.02285¦19.035503¦20.005964 | 0¦37.45214¦96.50579¦261.3702¦540.5289¦933.96387¦1441.6931¦1940.9479¦2241.2705¦2287.6167¦2291.6353¦2291.43¦2286.9827¦2291.0012¦2290.796¦2290.5815¦2290.3672¦2290.1528¦2289.9475
| Enercon E70 71m 2300kw | Enercon | 2310 |  |  | 71 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦2¦18¦56¦127¦240¦400¦626¦892¦1223¦1590¦1900¦2080¦2230¦2300¦2310¦2310¦2310¦2310¦2310¦2310¦2310¦2310¦2310¦2310¦0¦0¦0¦0¦0
| Bonus 82.4m 2.3MW | Bonus | 2311.11 |  |  | 82 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦0¦153.664¦301.182¦479.433¦731.442¦1008.04¦1346.1¦1745.63¦2034.52¦2200.47¦2274.23¦2298.82¦2311.11¦2311.11¦2311.11¦2311.11¦2311.11¦2311.11¦2311.11¦2311.11¦2311.11¦2304.97¦0¦0¦0¦0¦0
| Enercon E82 82m 2300kw | Enercon | 2350 |  |  | 82 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦25¦82¦174¦321¦532¦815¦1180¦1580¦1890¦2100¦2250¦2350¦2350¦2350¦2350¦2350¦2350¦2350¦2350¦2350¦2350¦2350¦2350¦0¦0¦0¦0¦0
| Mitsubishi MWT 92¦2.4 | Mitsubishi | 2400 |  |  | 92 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0.78¦34.62¦64.72¦94.81¦105.09¦154.79¦184.89¦214.76¦264.47¦314.18¦344.05¦403.55¦463.06¦512.53¦601.45¦680.56¦739.83¦818.94¦917.65¦1020¦1090¦1190¦1300¦1430¦1520¦1650¦1780¦1890¦1960¦2030¦2120¦2170¦2240¦2310¦2360¦2380¦2390¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Mitsubishi MWT 95¦2.4 | Mitsubishi | 2400 |  |  | 95 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0.78¦12.56¦41.92¦51.78¦81.14¦120.21¦139.78¦188.55¦237.33¦276.32¦334.81¦373.8¦432.28¦500.48¦549.18¦636.79¦685.49¦773.1¦860.72¦919.13¦1030¦1100¦1210¦1290¦1400¦1480¦1600¦1720¦1790¦1890¦1960¦2060¦2120¦2210¦2290¦2330¦2370¦2390¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦2400¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Fuhrlander FL 2500_100 | Fuhrlander | 2500 |  |  | 100 | [7 empty] | IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦32.69¦53.89¦75.09¦122.79¦159.89¦202.3¦239.4¦292.4¦345.41¦403.71¦472.6¦530.92¦594.52¦668.73¦727.03¦838.34¦933.75¦1030¦1140¦1260¦1390¦1530¦1650¦1780¦1930¦2050¦2180¦2250¦2330¦2400¦2470¦2480¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Fuhrlander FL 2500_80 | Fuhrlander | 2500 |  |  | 80 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦30¦69.79¦96.29¦122.79¦149.29¦175.8¦197¦228.8¦265.9¦313.6¦350.71¦398.41¦446.11¦499.12¦552.12¦599.81¦658.13¦742.93¦817.14¦891.34¦970.85¦1070¦1160¦1260¦1350¦1450¦1550¦1640¦1730¦1820¦1910¦2000¦2080¦2150¦2230¦2300¦2350¦2405¦2440¦2475¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Fuhrlander FL 2500_90 | Fuhrlander | 2500 |  |  | 90 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦30¦69.79¦96.29¦122.79¦165.19¦218.2¦255.3¦303¦361.31¦403.71¦462.01¦509.72¦568.02¦652.83¦727.03¦801.24¦891.34¦981.45¦1080¦1180¦1280¦1380¦1480¦1590¦1690¦1810¦1900¦2030¦2140¦2220¦2290¦2360¦2420¦2460¦2480¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| GE 2.5xl | GE | 2500 |  |  | 100 | [7 empty] | IIb¦IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦25.71¦37.14¦54.29¦77.14¦111.43¦145.71¦185.71¦231.43¦300¦334.29¦391.43¦454.29¦511.43¦602.85¦654.29¦734.29¦820¦905.71¦1000¦1070¦1170¦1280¦1380¦1510¦1640¦1790¦1920¦2010¦2110¦2190¦2260¦2320¦2370¦2420¦2460¦2480¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Liberty C89 | Liberty | 2500 |  |  | 89 | [7 empty] | Class Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦14.89¦29.34¦53.34¦72.53¦96.54¦125.35¦149.37¦197.49¦231.14¦264.79¦312.92¦365.87¦423.62¦476.56¦529.52¦587.3¦664.35¦741.41¦808.83¦890.72¦987.06¦1080¦1190¦1310¦1380¦1500¦1610¦1720¦1840¦1920¦2010¦2090¦2160¦2230¦2280¦2330¦2380¦2420¦2445¦2465¦2480¦2490¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Liberty C93 | Liberty | 2500 |  |  | 93 | [7 empty] | Class IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦24.56¦38.98¦58.17¦82.17¦111.01¦139.83¦173.49¦216.78¦255.26¦298.56¦356.32¦394.8¦462.22¦519.98¦572.93¦635.52¦717.4¦794.46¦905.29¦967.88¦1050¦1150¦1270¦1370¦1490¦1610¦1710¦1820¦1920¦2010¦2100¦2180¦2250¦2300¦2350¦2390¦2440¦2450¦2470¦2480¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Liberty C96 | Liberty | 2500 |  |  | 96 | [7 empty] | Class IIb | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦24.62¦43.81¦67.81¦96.64¦120.65¦149.48¦178.31¦231.25¦264.9¦308.21¦365.97¦418.92¦481.51¦548.92¦621.16¦693.4¦760.81¦876.46¦982.45¦1040¦1130¦1280¦1380¦1470¦1590¦1720¦1840¦1960¦2020¦2100¦2180¦2250¦2320¦2370¦2410¦2430¦2450¦2460¦2480¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Liberty C99 | Liberty | 2500 |  |  | 100 | [7 empty] | Class S | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦24.62¦34.16¦72.64¦106.29¦135.12¦159.12¦187.96¦240.89¦289.02¦327.5¦390.08¦452.68¦510.45¦573.05¦654.92¦727.16¦809.05¦876.46¦987.27¦1120¦1210¦1320¦1440¦1550¦1660¦1770¦1880¦1980¦2100¦2180¦2240¦2300¦2350¦2390¦2420¦2440¦2460¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Liberty Clipper C100 100m 2500kw | Liberty | 2500 |  |  | 100 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦96¦221¦412¦669¦993¦1456¦1882¦2235¦2419¦2485¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0
| Nordex N100-2500 | Nordex | 2500 |  |  | 100 | [7 empty] | IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦12.5¦25¦37.5¦50¦92.75¦135.5¦178.25¦221¦273.5¦326¦378.5¦431¦503.25¦575.5¦647.75¦720¦815.5¦911¦1006.5¦1102¦1220.25¦1338.5¦1456.75¦1575¦1686¦1797¦1908¦2019¦2090.25¦2161.5¦2232.75¦2304¦2342.5¦2381¦2419.5¦2458¦2468.5¦2479¦2489.5¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N80-2500 | Nordex | 2500 |  |  | 80 | [7 empty] | I | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦3.75¦7.5¦11.25¦15¦41.5¦68¦94.5¦121¦153.5¦186¦218.5¦251¦296.5¦342¦387.5¦433¦491.5¦550¦608.5¦667¦743.75¦820.5¦897.25¦974¦1060.25¦1146.5¦1232.75¦1319¦1408¦1497¦1586¦1675¦1757.25¦1839.5¦1921.75¦2004¦2073.25¦2142.5¦2211.75¦2281¦2326.5¦2372¦2417.5¦2463¦2472.25¦2481.5¦2490.75¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N90-2500 HS | Nordex | 2500 |  |  | 90 | [7 empty] | Ia | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦5¦22.5¦40¦71.5¦103¦136.5¦170¦209.5¦249¦295¦341¦394.5¦448¦510¦572¦644¦716¦798¦880¦971¦1062¦1162¦1262¦1368.5¦1475¦1588.5¦1702¦1815¦1928¦2022¦2116¦2189¦2262¦2316¦2370¦2406.5¦2443¦2471.5¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Nordex N90-2500 LS | Nordex | 2500 |  |  | 90 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦5¦20¦35¦66.5¦98¦136.5¦175¦217.5¦260¦306¦352¦407¦462¦521¦580¦648.5¦717¦793.5¦870¦957.5¦1045¦1141¦1237¦1333.5¦1430¦1526.5¦1623¦1729¦1835¦1939¦2043¦2121.5¦2200¦2272.5¦2345¦2387.5¦2430¦2452.5¦2475¦2482.5¦2490¦2495¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vensys 100m 2500kW | Vensys | 2500 |  |  | 100 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦125.5¦250.1¦437.4¦696.4¦1034.8¦1449.3¦1904.1¦2285.5¦2472.1¦2499.4¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0
| Vensys 109m 2500kW | Vensys | 2500 |  |  | 109 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦151.2¦298.1¦518.2¦821.7¦1222.8¦1720.1¦2193¦2448.7¦2494.2¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0
| Vensys 112m 2500kW | Vensys | 2500 |  |  | 112 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦154.2¦315.9¦548.5¦871.1¦1290.1¦1808.8¦2269.5¦2465.1¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦2500¦0¦0¦0¦0¦0
| Leitwind LTW101m 3MW | Leitwind | 3000 |  |  | 100 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦41¦124¦257¦456¦735¦1101¦1537¦2019¦2543¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦0¦0¦0¦0¦0
| Senvion 3mW 122m | Senvion | 3000 |  |  | 122 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦158¦384¦696¦1149¦1744¦2444¦2821¦2991¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦0¦0¦0¦0¦0¦0¦0¦0
| Siemens SWT-3.0MW-101m | Siemens | 3000 |  |  | 101 | [7 empty] | unknown | 3¦3.0084422¦4.002302¦4.996163¦6.0168843¦6.9838834¦7.9777436¦8.998466¦9.992326¦11.013047¦12.006907¦13.027629¦13.994628¦14.961627¦16.03607¦17.003069¦18.02379¦19.017653¦20.038372¦21.005373¦21.999233¦23.019955¦24.013815¦25.034536 | 0¦7.490637¦119.85019¦262.17227¦434.45694¦719.10114¦1093.6329¦1565.5431¦2082.397¦2554.3071¦2876.4045¦2981.2734¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546¦2996.2546
| Vestas V112-3.0 | Vestas | 3000 |  |  | 112 | [7 empty] | IIa¦IIIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦72.12¦83.65¦106.73¦135.58¦170.19¦204.81¦245.19¦297.12¦337.5¦389.42¦441.35¦504.81¦568.27¦643.27¦729.81¦816.35¦925.96¦1050¦1170¦1300¦1420¦1540¦1680¦1810¦1960¦2110¦2270¦2430¦2560¦2700¦2810¦2880¦2930¦2960¦2980¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Vestas V90-3.0 | Vestas | 3000 |  |  | 90 | [7 empty] | Ia¦IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦26.4425¦52.885¦88.1416666666667¦105.77¦129.41¦153.12¦182.53¦211.94¦247.12¦282.3¦317.48¦370.05¦422.54¦469.26¦515.98¦580.01¦644.03¦713.83¦795.17¦888.05¦992.55¦1090¦1200¦1290¦1380¦1470¦1560¦1650¦1750¦1850¦1950¦2030¦2140¦2230¦2340¦2440¦2540¦2640¦2730¦2790¦2850¦2890¦2910¦2940¦2970¦2990¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦3000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Enercon E82 82m 3000kw | Enercon | 3020 |  |  | 82 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦25¦82¦174¦321¦532¦815¦1180¦1580¦1900¦2200¦2480¦2700¦2850¦2950¦3020¦3020¦3020¦3020¦3020¦3020¦3020¦3020¦3020¦0¦0¦0¦0¦0
| Enercon E101 101m 3000kw | Enercon | 3050 |  |  | 101 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦37¦118¦258¦479¦790¦1200¦1710¦2340¦2867¦3034¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦3050¦0¦0¦0¦0¦0
| Senvion 3.2mW 114m | Senvion | 3200 |  |  | 114 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦128¦311¦576¦959¦1453¦2056¦2659¦3070¦3200¦3200¦3200¦3200¦3200¦3200¦3200¦3200¦3200¦3200¦3200¦0¦0¦0¦0¦0¦0¦0¦0
| RePower 3XM | RePower | 3300 |  |  | 104 | [7 empty] | IIa | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦47.35¦94.7¦125¦162.88¦208.33¦253.79¦299.24¦352.27¦405.3¦465.91¦541.67¦602.27¦678.03¦761.35¦844.7¦943.18¦1040¦1130¦1250¦1370¦1490¦1610¦1720¦1860¦2000¦2130¦2250¦2370¦2510¦2630¦2750¦2850¦2960¦3060¦3160¦3260¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦3300¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Senvion 3.4mW 114m | Senvion | 3400 |  |  | 114 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦96¦254¦482¦782¦1196¦1707¦2253¦2780¦3250¦3393¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦0¦0¦0¦0¦0
| Senvion 3.4mW 114m | Senvion | 3400 |  |  | 114 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦128¦315¦567¦932¦1429¦2000¦2619¦3116¦3340¦3393¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦3400¦0¦0¦0¦0¦0¦0¦0¦0
| General Electric GE 3.6sl 111m 3600kwn | General | 3600 |  |  | 111 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦98¦244¦451¦732¦1110¦1574¦2184¦2721¦3148¦3417¦3563¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦0¦0¦0
| Siemens 3.6 MW 120 m | Siemens | 3600 |  |  | 120 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦127¦285¦512¦795¦1140¦1587¦2120¦2770¦3287¦3500¦3578¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦0¦0¦0¦0¦0
| Siemens SWT-3.6MW-107m | Siemens | 3600 |  |  | 107 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦113¦296¦523¦827¦1159¦1594¦2135¦2788¦3285¦3485¦3564¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦3600¦0¦0¦0¦0¦0
| Gamesa G128 4.5MW | Gamesa | 4500 |  |  | 128 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦222¦444¦777¦1206¦1857¦2603¦3460¦4158¦4412¦4500¦4500¦4500¦4500¦4500¦4500¦4380¦4238¦4063¦3873¦3666¦3444¦3285¦3047¦2857¦0¦0¦0
| Areva Multibrid m5000 | Areva | 5000 |  |  | 116 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦25¦50¦107.5¦165¦222.5¦280¦345¦410¦475¦540¦622.5¦705¦787.5¦870¦986.25¦1102.5¦1218.75¦1335¦1482.5¦1630¦1777.5¦1925¦2097.5¦2270¦2442.5¦2615¦2865¦3115¦3365¦3615¦3910¦4205¦4500¦4795¦4897.5¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| BARD 5.0 | BARD | 5000 |  |  | 122 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦15¦30¦45¦60¦103.75¦147.5¦191.25¦235¦308.75¦382.5¦456.25¦530¦632.5¦735¦837.5¦940¦1072.5¦1205¦1337.5¦1470¦1676.25¦1882.5¦2088.75¦2295¦2493.75¦2692.5¦2891.25¦3090¦3317.5¦3545¦3772.5¦4000¦4220¦4440¦4660¦4880¦4940¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| NREL 5MW Offshore Reference | NREL | 5000 |  |  | 112 | [7 empty] | IIa¦IIIa | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦40 | 0¦0¦0¦40.5¦177.7¦403.9¦737.6¦1187.2¦1771.1¦2518.6¦3448.4¦4562.5¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦5000.0¦0.0¦0.0
| RePower 5M | RePower | 5000 |  |  | 126 | [7 empty] | unknown | 0¦0.25¦0.5¦0.75¦1¦1.25¦1.5¦1.75¦2¦2.25¦2.5¦2.75¦3¦3.25¦3.5¦3.75¦4¦4.25¦4.5¦4.75¦5¦5.25¦5.5¦5.75¦6¦6.25¦6.5¦6.75¦7¦7.25¦7.5¦7.75¦8¦8.25¦8.5¦8.75¦9¦9.25¦9.5¦9.75¦10¦10.25¦10.5¦10.75¦11¦11.25¦11.5¦11.75¦12¦12.25¦12.5¦12.75¦13¦13.25¦13.5¦13.75¦14¦14.25¦14.5¦14.75¦15¦15.25¦15.5¦15.75¦16¦16.25¦16.5¦16.75¦17¦17.25¦17.5¦17.75¦18¦18.25¦18.5¦18.75¦19¦19.25¦19.5¦19.75¦20¦20.25¦20.5¦20.75¦21¦21.25¦21.5¦21.75¦22¦22.25¦22.5¦22.75¦23¦23.25¦23.5¦23.75¦24¦24.25¦24.5¦24.75¦25¦25.25¦25.5¦25.75¦26¦26.25¦26.5¦26.75¦27¦27.25¦27.5¦27.75¦28¦28.25¦28.5¦28.75¦29¦29.25¦29.5¦29.75¦30¦30.25¦30.5¦30.75¦31¦31.25¦31.5¦31.75¦32¦32.25¦32.5¦32.75¦33¦33.25¦33.5¦33.75¦34¦34.25¦34.5¦34.75¦35¦35.25¦35.5¦35.75¦36¦36.25¦36.5¦36.75¦37¦37.25¦37.5¦37.75¦38¦38.25¦38.5¦38.75¦39¦39.25¦39.5¦39.75¦40.00 | 0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦20¦50¦93.75¦137.5¦181.25¦225¦301.25¦377.5¦453.75¦530¦632.5¦735¦837.5¦940¦1072.5¦1205¦1337.5¦1470¦1637.5¦1805¦1972.5¦2140¦2340¦2540¦2740¦2940¦3163.75¦3387.5¦3611.25¦3835¦4013.75¦4192.5¦4371.25¦4550¦4637.5¦4725¦4812.5¦4900¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦5000¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0¦0
| Senvion 6.2M152 offshore | Senvion | 6150 |  |  | 152 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦82¦411¦873¦1550¦2524¦3695¦5082¦5974¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150¦6150
| Senvion 6.2M126 offshore | Senvion | 6200 |  |  | 126 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦68¦322¦661¦1100¦1659¦2369¦3198¦4145¦5025¦5735¦6124¦6160¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200¦6200
| Vestas V-164 7mW offshore | Vestas | 7000 |  |  | 164 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦92¦474¦910¦1569¦2500¦3726¦5004¦5991¦6715¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦7000¦0¦0¦0¦0¦0
| Enercon E-126 127m 7500kW | Enercon | 7500 |  |  | 127 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦55¦175¦410¦760¦1250¦1900¦2700¦3750¦4850¦5750¦6500¦7000¦7350¦7500¦7500¦7500¦7500¦7500¦7500¦7500¦7500¦7500¦7500¦0¦0¦0¦0¦0
| Vestas 164 8mW | Vestas | 8000 |  |  | 164 | [7 empty] | unknown | 1¦2¦3¦4¦5¦6¦7¦8¦9¦10¦11¦12¦13¦14¦15¦16¦17¦18¦19¦20¦21¦22¦23¦24¦25¦26¦27¦28¦29¦30 | 0¦0¦0¦192¦596¦1135¦1866¦2942.31¦4212¦5673¦7135¦7885¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦8000¦0¦0¦0¦0¦0
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Based on SAM Name (column B) or PNNL information.

## Skystream 3.7 (Xzeres)
Source: | Small Wind Certification Council (SWCC) Summary Report
PNNL has copy of report
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 1 | 0.56 | -0.018
2 | 0 | 2 | 1.04 | -0.018
3 | 0 | 3 | 1.52 | -0.018
4 | 0.084 | 4 | 2.02 | -0.017
5 | 0.203 | 5 | 2.51 | -0.012
6 | 0.391 | 6 | 3 | 0.003
7 | 0.643 | 7 | 3.51 | 0.034
8 | 0.968 | 8 | 4.03 | 0.084
9 | 1.333 | 9 | 4.46 | 0.132
10 | 1.748 | 10 | 5 | 0.203
11 | 2.106 | 11 | 5.49 | 0.285
12 | 2.301 | 12 | 6 | 0.391
13 | 2.403 | 13 | 6.5 | 0.51
14 | 2.425 | 14 | 6.99 | 0.643
15 | 2.414 | 15 | 7.49 | 0.799
16 | 2.4 | 16 | 7.99 | 0.968
17 | 2.3 | 17 | 8.5 | 1.146
18 | 2.265 | 18 | 8.99 | 1.333
19 | 2.203 | 19 | 9.48 | 1.531
20 | 2.203 | 20 | 9.98 | 1.745
21 | 2.203 | 21 | 10.47 | 1.938
22 | 2.203 | 22 | 10.97 | 2.101
23 | 2.203 | 23 | 11.47 | 2.242
24 | 2.203 | 24 | 11.93 | 2.301
25 | 2.203 | 25 | 12.45 | 2.363
26 | 0 | 26 | 12.97 | 2.403
27 | 0 | 27 | 13.5 | 2.403
28 | 0 | 28 | 13.99 | 2.435
29 | 0 | 29 | 14.52 | 2.388
30 | 0 | 30 | 15.02 | 2.412
|  | 31 | 15.45 | 2.403
|  | 32 | 15.99 | 2.393
|  | 33 | 16.5 | 2.321

## Endurance Wind S-343
Source: | SWCC Limited Power Performance Report
PNNL has copy
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
0 | 0 | 1 | 0.5 | -0.038
2 | 0 | 2 | 1 | -0.042
4 | 0 | 3 | 1.5 | -0.046
6 | 1.15 | 4 | 2 | -0.046
8 | 3.2 | 5 | 2.5 | -0.051
10 | 4.9 | 6 | 3 | -0.05
12 | 5.3 | 7 | 3.5 | -0.098
14 | 4.95 | 8 | 4 | -0.094
16 | 3.85 | 9 | 4.5 | -0.003
18 | 3 | 10 | 5 | 0.285
20 | 1 | 11 | 5.5 | 0.745
21 | 0 | 12 | 6 | 1.01
40 | 0 | 13 | 6.5 | 1.43
|  | 14 | 7 | 1.972
|  | 15 | 7.5 | 2.483
|  | 16 | 8 | 3.04
|  | 17 | 8.5 | 3.581
|  | 18 | 9 | 4.042
|  | 19 | 9.5 | 4.483
|  | 20 | 10 | 4.838
|  | 21 | 10.5 | 5.141
|  | 22 | 11 | 5.402
|  | 23 | 11.5 | 5.645
|  | 24 | 12 | 5.845
|  | 25 | 12.5 | 5.958
|  | 26 | 13 | 6.002
|  | 27 | 13.5 | 5.915
|  | 28 | 14 | 5.756
|  | 29 | 14.5 | 5.515
|  | 30 | 15 | 5.236
|  | 31 | 15.5 | 4.914
|  | 32 | 16 | 4.603
|  | 33 | 16.5 | 4.249
|  | 34 | 17 | 3.905

## Evance R9000
Source: | UK MCS Certification Summary
PNNL has copy
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 1 | 0.59 | 0.009
2 | 0 | 2 | 1 | 0.005
3 | 0 | 3 | 1.53 | -0.003
4 | 0.21 | 4 | 2.03 | -0.004
5 | 0.576 | 5 | 2.5 | -0.002
6 | 1.104 | 6 | 3 | 0.013
7 | 1.783 | 7 | 3.53 | 0.073
8 | 2.542 | 8 | 4 | 0.201
9 | 3.349 | 9 | 4.51 | 0.385
10 | 4.077 | 10 | 5 | 0.619
11 | 4.628 | 11 | 5.5 | 0.864
12 | 4.911 | 12 | 6 | 1.174
13 | 5.066 | 13 | 6.5 | 1.508
14 | 5.141 | 14 | 7 | 1.894
15 | 5.142 | 15 | 7.5 | 2.271
16 | 5.159 | 16 | 8.01 | 2.71
17 | 5.217 | 17 | 8.5 | 3.15
18 | 5.212 | 18 | 9 | 3.523
19 | 5.242 | 19 | 9.5 | 3.918
20 | 5.235 | 20 | 10 | 4.244
21 | 5.235 | 21 | 10.49 | 4.496
22 | 5.235 | 22 | 10.99 | 4.711
23 | 5.235 | 23 | 11.49 | 4.834
24 | 5.235 | 24 | 11.99 | 4.929
25 | 5.235 | 25 | 12.48 | 4.975
26 | 5.235 | 26 | 12.99 | 4.971
27 | 5.235 | 27 | 13.49 | 4.972
28 | 5.235 | 28 | 13.99 | 4.974
29 | 5.235 | 29 | 14.49 | 4.931
30 | 5.235 | 30 | 14.96 | 4.965
|  | 31 | 15.49 | 5.014
|  | 32 | 15.98 | 5.079
|  | 33 | 16.47 | 5.096
|  | 34 | 17 | 5.073
|  | 35 | 17.42 | 5.056
|  | 36 | 17.91 | 5.072
|  | 37 | 18.4 | 5.026
|  | 38 | 19.13 | 5.123

## SD6
Source: | SWCC Summary Report
As of February 2020 http://smallwindcertification.org/certified-turbines/sd6
PNNL has copy
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 1 | 0.56 | 0
2 | 0 | 2 | 2 | 0
3 | 0 | 3 | 2.43 | -2
4 | 0.172 | 4 | 2.07 | -1
5 | 0.485 | 5 | 2.54 | 12
6 | 1.02 | 6 | 3.05 | 45
7 | 1.733 | 7 | 3.52 | 96
8 | 2.674 | 8 | 3.98 | 172
9 | 3.546 | 9 | 4.49 | 296
10 | 4.428 | 10 | 4.99 | 485
11 | 5.164 | 11 | 5.5 | 739
12 | 5.626 | 12 | 5.99 | 1020
13 | 5.96 | 13 | 6.49 | 1326
14 | 6.026 | 14 | 7 | 1733
15 | 6.059 | 15 | 7.5 | 2165
16 | 6.099 | 16 | 8 | 2674
17 | 6.136 | 17 | 8.5 | 3121
18 | 6.1 | 18 | 8.98 | 3546
19 | 5.952 | 19 | 9.49 | 4033
20 | 5.988 | 20 | 10.01 | 4428
21 | 5.8 | 21 | 10.5 | 4870
22 | 5.8 | 22 | 10.99 | 5164
23 | 5.8 | 23 | 11.51 | 5464
24 | 5.8 | 24 | 11.99 | 5626
25 | 5.8 | 25 | 12.49 | 5851
26 | 5.8 | 26 | 12.98 | 5960
27 | 5.8 | 27 | 13.5 | 6000
28 | 5.8 | 28 | 13.98 | 6026
29 | 5.8 | 29 | 14.5 | 6064
30 | 5.8 | 30 | 15 | 6059
|  | 31 | 15.5 | 6119
|  | 32 | 15.99 | 6099

## Bergey Excel 10
Source: | SWCC Summary Report
As of February 2020 http://smallwindcertification.org/certified-turbines/excel-10
PNNL also has copy of report
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) |  | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 1 | 0.5 | -0.012
2 | 0 | 2 | 1 | -0.012
3 | 0.102 | 3 | 1.5 | -0.011
4 | 0.399 | 4 | 2 | 0
5 | 0.848 | 5 | 2.5 | 0.039
6 | 1.51 | 6 | 3 | 0.102
7 | 2.403 | 7 | 3.5 | 0.229
8 | 3.602 | 8 | 4 | 0.399
9 | 5.071 | 9 | 4.5 | 0.596
10 | 6.856 | 10 | 5 | 0.848
11 | 8.863 | 11 | 5.5 | 1.151
12 | 10.885 | 12 | 6 | 1.51
13 | 12.019 | 13 | 6.5 | 1.938
14 | 12.395 | 14 | 7 | 2.403
15 | 12.495 | 15 | 7.5 | 2.949
16 | 12.546 | 16 | 8 | 3.602
17 | 12.503 | 17 | 8.5 | 4.306
18 | 12.442 | 18 | 9 | 5.071
19 | 12.208 | 19 | 9.5 | 5.96
20 | 11.989 | 20 | 10 | 6.856
21 | 11.6 | 21 | 10.5 | 7.849
22 | 11.2 | 22 | 11 | 8.863
23 | 10.8 | 23 | 11.5 | 9.928
24 | 10.4 | 24 | 12 | 10.885
25 | 10 | 25 | 12.5 | 11.619
26 | 9.6 | 26 | 13 | 12.019
27 | 9.2 | 27 | 13.5 | 12.276
28 | 8.8 | 28 | 14 | 12.395
29 | 8.4 | 29 | 14.5 | 12.449
30 | 8 | 30 | 15 | 12.495
|  | 31 | 15.5 | 12.508
|  | 32 | 16 | 12.546
|  | 33 | 16.5 | 12.555
|  | 34 | 17 | 12.503
|  | 35 | 17.5 | 12.528
|  | 36 | 18 | 12.442
|  | 37 | 18.5 | 12.396
|  | 38 | 19 | 12.208
|  | 39 | 19.5 | 11.878
|  | 40 | 20 | 11.989
|  | 41 | 20.5 | 11.495

## Gaia 133-11kW
Source: | UK MCS Summary Report
PNNL has copy
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 1 | 0.64 | -0.03
2 | 0 | 2 | 1.06 | -0.03
3 | 0 | 3 | 1.53 | -0.03
4 | 1.1 | 4 | 2.02 | -0.03
5 | 2.8 | 5 | 2.5 | -0.05
6 | 5 | 6 | 3.01 | -0.12
7 | 7.3 | 7 | 3.51 | 0.08
8 | 8.9 | 8 | 4 | 0.71
9 | 10.4 | 9 | 4.49 | 1.56
10 | 11.4 | 10 | 4.99 | 2.46
11 | 11.79 | 11 | 5.49 | 3.44
12 | 11.4 | 12 | 5.99 | 4.43
13 | 10.96 | 13 | 6.49 | 5.44
14 | 10.07 | 14 | 6.98 | 6.3
15 | 9.35 | 15 | 7.48 | 7.14
16 | 8.96 | 16 | 7.98 | 7.91
17 | 8.96 | 17 | 8.49 | 8.61
18 | 8.8 | 18 | 8.98 | 9.16
19 | 8.47 | 19 | 9.46 | 9.67
20 | 8.08 | 20 | 9.99 | 10.29
21 | 7.75 | 21 | 10.5 | 10.51
22 | 7.47 | 22 | 11.02 | 10.69
23 | 7.19 | 23 | 11.51 | 10.81
24 | 6.81 | 24 | 12.02 | 10.93
25 | 6.42 | 25 | 12.51 | 10.67
26 | 0 | 26 | 12.97 | 10.74
27 | 0 | 27 | 13.52 | 10.47
28 | 0 | 28 | 14.06 | 10.26
29 | 0 | 29 | 14.53 | 9.82
30 | 0 | 30 | 14.98 | 9.54
|  | 31 | 15.52 | 9.42
|  | 32 | 16 | 8.79
|  | 33 | 16.5 | 9.07
|  | 34 | 16.98 | 8.76
|  | 35 | 17.5 | 8.69
|  | 36 | 17.89 | 7.91
|  | 37 | 18.42 | 8.69
|  | 38 | 19.24 | 8.12
|  | 39 | 19.5 | 0
|  | 40 | 20 | 0
|  | 41 | 20.5 | 0
|  | 42 | 21 | 0
|  | 43 | 21.5 | 0
|  | 44 | 22 | 0
|  | 45 | 22.5 | 0
|  | 46 | 23 | 0
|  | 47 | 23.5 | 0
|  | 48 | 24 | 0
|  | 49 | 24.5 | 0
|  | 50 | 25 | 0

## Jacobs 31-20
Source: | Intertek report
PNNL has a copy
SAM |  |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) |  | Hub Height Wind Speed (m/s) | Power Output (kW)
0 | 0 | 1 | 0.51 | -0.04
1 | 0 | 2 | 1.05 | -0.04
2 | 0 | 3 | 1.55 | -0.04
3 | 0 | 4 | 2.01 | -0.04
3.35 | 0 | 5 | 2.5 | -0.04
4 | 0 | 6 | 2.99 | -0.02
5 | 1.59 | 7 | 3.52 | 0.03
6 | 2.75 | 8 | 4 | 0.17
7 | 4.37 | 9 | 4.51 | 0.35
8 | 6.53 | 10 | 5.01 | 0.66
9 | 9.29 | 11 | 5.5 | 1.07
10 | 12.75 | 12 | 5.99 | 1.6
11 | 16.97 | 13 | 6.5 | 2.19
11.62 | 20 | 14 | 7 | 2.97
12 | 20 | 15 | 7.51 | 3.84
13 | 20 | 16 | 8.01 | 4.63
14 | 20 | 17 | 8.49 | 5.58
15 | 20 | 18 | 9 | 6.67
16 | 20 | 19 | 9.49 | 7.91
17 | 20 | 20 | 10 | 9.19
18 | 20 | 21 | 10.5 | 10.62
19 | 20 | 22 | 10.99 | 12
20 | 20 | 23 | 11.5 | 13.14
21 | 20 | 24 | 11.98 | 14.48
22 | 20 | 25 | 12.5 | 15.72
23 | 20 | 26 | 13.99 | 18.28
24 | 20 | 27 | 14.5 | 18.62
25 | 20 | 28 | 14.99 | 19.06
26 | 20 | 29 | 15.5 | 19.2
27 | 20 | 30 | 15.98 | 19.54
28 | 20 | 31 | 16.49 | 19.58
29 | 20 | 32 | 16.97 | 19.78
30 | 20 | 33 | 17.49 | 19.91
31 | 0 | 34 | 17.99 | 20
40 | 0 | 35 | 18.49 | 20.03
|  | 36 | 19.06 | 19.66
|  | 37 | 19.44 | 19.98
|  | 38 | 19.97 | 19.84
|  | 39 | 20.51 | 20.12
|  | 40 | 21.04 | 20.18

## Eocycle E025
Source: | SGS Certificate
PNNL has a copy
SAM |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 3 | 0.38
2 | 0 | 3.5 | 1.24
3 | 0 | 4 | 2.28
4 | 0.96 | 4.5 | 3.66
5 | 2.82 | 5 | 5.49
6 | 5.7 | 5.5 | 7.44
7 | 9.81 | 6 | 9.87
8 | 15.25 | 6.5 | 12.71
9 | 20.53 | 7 | 15.55
10 | 23.51 | 7.5 | 18.44
11 | 25 | 8 | 21.05
12 | 25.95 | 8.5 | 23.08
13 | 26.6 | 9 | 24.95
14 | 27.2 | 9.5 | 26.44
15 | 27.56 | 10 | 27.64
16 | 27.64 | 10.5 | 28.46
17 | 27.31 | 11 | 28.89
18 | 26.37 | 11.5 | 29.16
19 | 24.77 | 12 | 29.19
20 | 21.68 | 12.5 | 28.91
21 | 17.17 | 13 | 28.77
22 | 13.19 | 13.5 | 27.74
23 | 10.83 | 14 | 26.88
24 | 11.33 | 14.5 | 25.17
25 | 12.16 | 15 | 24.3
26 | 0 | 15.5 | 23.48
27 | 0 | 16 | 22
28 | 0 | 16.5 | 20.53
29 | 0 | 17 | 20.2
30 | 0 | 17.5 | 19.64
|  | 18 | 19.64
|  | 18.5 | 19.64
|  | 19 | 19.64
|  | 19.5 | 19.64
|  | 20 | 19.64

## Endurance E-3120
Source: | SWCC Power Performance Summary Report
PNNL has copy
SAM
Wind Speed Array (m/s) | Power Curve Array (kW) | Hub Height Wind Speed (m/s) | Power Output (kW)
0 | 0 | 0.5
1 | 0 | 1
2 | 0 | 1.5 | -0.14
3 | 0 | 2 | -0.33
4 | 2 | 2.5 | -0.24
5 | 9 | 3 | -0.09
6 | 15 | 3.5 | 1.03
7 | 25 | 4 | 2.48
8 | 36 | 4.5 | 4.71
9 | 44 | 5 | 8.21
10 | 51 | 5.5 | 11.82
11 | 55 | 6 | 16.19
12 | 57 | 6.5 | 20.17
13 | 59.5 | 7 | 25.04
14 | 59 | 7.5 | 29.26
15 | 58 | 8 | 35.07
16 | 57 | 8.5 | 39.69
17 | 55 | 9 | 43.96
18 | 50 | 9.5 | 47.67
19 | 44 | 10 | 51.52
20 | 37 | 10.5 | 54.73
21 | 0 | 11 | 56.84
40 | 0 | 11.5 | 58.92
|  | 12 | 60.25
|  | 12.5 | 61.25
|  | 13 | 62.1
|  | 13.5 | 62.67
|  | 14 | 63.38
|  | 14.5 | 63.62
|  | 15 | 65.02
|  | 15.5 | 65.47
|  | 16 | 65.67
|  | 16.5 | 66.57
|  | 16.9 | 67.46

## NPS 100-24
Source: | DNV Power Performance Test Report
PNNL has a copy
SAM |  | CERTIFIED
Wind Speed Array (m/s) | Power Curve Array (kW) | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0 | 0.22 | -0.4
2 | 0 | 0.58 | -0.5
3 | 0.9 | 1.04 | -0.5
4 | 5 | 1.54 | -0.5
5 | 11.7 | 2.02 | -0.5
6 | 22.2 | 2.5 | -0.3
7 | 35.5 | 3 | 0.6
8 | 49.9 | 3.52 | 2.3
9 | 63.4 | 4.01 | 4.6
10 | 74.7 | 4.5 | 7.1
11 | 83.5 | 5 | 10.4
12 | 89.7 | 5.5 | 14.3
13 | 93.7 | 6 | 18.9
14 | 95.5 | 6.49 | 24.4
15 | 95.2 | 7 | 30.7
16 | 92.5 | 7.51 | 37.6
17 | 87.7 | 8 | 43.9
18 | 81.1 | 8.5 | 51.1
19 | 73.8 | 8.98 | 57.4
20 | 67.3 | 9.5 | 63.8
21 | 62.4 | 10 | 69.4
22 | 57.7 | 10.49 | 75.1
23 | 54 | 10.98 | 79.2
24 | 50.6 | 11.47 | 84
25 | 47.4 | 11.98 | 87.4
26 | 0 | 12.43 | 90.7
27 | 0 | 13.01 | 95.7
28 | 0 | 13.55 | 97.8
29 | 0 | 13.92 | 103.6
30 | 0 | 14.46 | 104.4
|  | 14.81 | 103.4
|  | 15.4 | 97.7

## NPS 100-21
Source: | 2015 Manufacturer Spec Sheet
PNNL has a copy
SAM |  | MANUFACTURER
Wind Speed Array (m/s) | Power Curve Array (kW) | Hub Height Wind Speed (m/s) | Power Output (kWe)
0 | 0 | 1 | -0.6
1 | 0 | 2 | -0.6
2 | 0 | 3 | 0.5
3 | 0 | 4 | 4.1
4 | 3.7 | 5 | 10.5
5 | 10.5 | 6 | 19
6 | 19 | 7 | 29.4
7 | 29.4 | 8 | 41
8 | 41 | 9 | 54.3
9 | 54.3 | 10 | 66.8
10 | 66.8 | 11 | 77.7
11 | 77.7 | 12 | 86.4
12 | 86.4 | 13 | 92.8
13 | 92.8 | 14 | 97.8
14 | 97.3 | 15 | 100
15 | 100 | 16 | 99.9
16 | 100.8 | 17 | 99.2
17 | 100.6 | 18 | 98.4
18 | 99.8 | 19 | 97.5
19 | 99.4 | 20 | 96.8
20 | 98.6 | 21 | 96.4
21 | 97.8 | 22 | 96.3
22 | 97.3 | 23 | 96.8
23 | 97.3 | 24 | 98
24 | 98 | 25 | 99.2
25 | 99.7
26 | 0
27 | 0
28 | 0
29 | 0
30 | 0
31 | 0
32 | 0
33 | 0
34 | 0
35 | 0
36 | 0
37 | 0
38 | 0
39 | 0
40 | 0

## XANT M-21
Source: | Tuv-Sud Test Report
PNNL has a copy
CERTIFIED
| Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
0.5
1
1.5
2
| 2.5 | 2.73 | 0.95
| 3 | 3.12 | 2.86
| 3.5 | 3.59 | 2.34
| 4 | 4.01 | 3.87
| 4.5 | 4.49 | 6.46
| 5 | 4.97 | 9.65
| 5.5 | 5.49 | 14.12
| 6 | 5.97 | 18.52
| 6.5 | 6.5 | 24.94
| 7 | 6.98 | 29.66
| 7.5 | 7.53 | 38.42
| 8 | 7.99 | 46.29
| 8.5 | 8.52 | 51.49
| 9 | 9.03 | 62.87
| 9.5 | 9.45 | 68.97
| 10 | 10.01 | 83.67
| 10.5 | 10.48 | 90.14
| 11 | 10.99 | 96.78
| 11.5 | 11.7 | 100.47
| 12 | 11.82 | 104.69
| 12.5 | 12.48 | 103.29

## Bergey Excel 15
Source: | SWCC Summary Report (Limited Power Performance)
As of February 2020 http://smallwindcertification.org/certified-turbines/excel-15
PNNL has a copy
SAM |  | CERTIFIED
Wind Speed Array (m/s) | Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 1 | 1 | -0.029
2 | 1.5 | 1.51 | -0.028
3 | 2 | 2.01 | -0.025
4 | 2.5 | 2.52 | 0
5 | 3 | 2.99 | 0.108
6 | 3.5 | 3.49 | 0.328
7 | 4 | 4.01 | 0.679
8 | 4.5 | 4.51 | 1.28
9 | 5 | 5 | 2.074
10 | 5.5 | 5.5 | 2.878
11 | 6 | 6 | 3.824
12 | 6.5 | 6.5 | 4.897
13 | 7 | 7 | 6.089
14 | 7.5 | 7.49 | 7.226
15 | 8 | 8 | 8.5
16 | 8.5 | 8.5 | 9.731
17 | 9 | 9 | 11.265
18 | 9.5 | 9.49 | 12.361
19 | 10 | 9.99 | 13.664
20 | 10.5 | 10.51 | 14.502
21 | 11 | 11.01 | 15.612
22 | 11.5 | 11.48 | 16.304
23 | 12 | 11.97 | 16.876
24 | 12.5 | 12.51 | 17.506
25 | 13 | 12.99 | 18.212
26 | 13.5 | 13.5 | 18.942
27 | 14 | 13.99 | 19.096
28 | 14.5 | 14.48 | 19.6
29 | 15 | 15 | 20.355
30 | 15.5 | 15.51 | 20.251
| 16 | 15.97 | 20.611
| 16.5 | 16.47 | 19.687

## Hi VAWT DS3000
Source: | SWCC Summary Report
As of February 2020 http://smallwindcertification.org/certified-turbines/ds3000
PNNL has a copy
CERTIFIED
Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 0.57 | -0.0225
2 | 1.01 | -0.0224
3 | 1.53 | -0.0224
4 | 2.02 | -0.0223
5 | 2.5 | -0.0195
6 | 2.98 | -0.0062
7 | 3.49 | 0.0192
8 | 4 | 0.0518
9 | 4.5 | 0.0949
10 | 4.99 | 0.1494
11 | 5.5 | 0.2186
12 | 5.99 | 0.2958
13 | 6.5 | 0.398
14 | 6.99 | 0.5002
15 | 7.49 | 0.623
16 | 7.97 | 0.7517
17 | 8.49 | 0.9265
18 | 9 | 1.0934
19 | 9.5 | 1.2391
20 | 9.99 | 1.3605
21 | 10.5 | 1.4356
22 | 10.99 | 1.4329
23 | 11.5 | 1.2491
24 | 11.98 | 1.0911
25 | 12.51 | 0.7838
26 | 13 | 0.6997
27 | 13.48 | 0.52
28 | 13.96 | 0.5161
29 | 14.5 | 0.2512
30 | 14.95 | 0.444
31 | 15.46 | 0.2056
32 | 15.93 | 0.2602

## Ghrepower FD21-50
Source: | SWCC Summary Report
As of February 2020 http://smallwindcertification.org/certified-turbines/fd21-50
PNNL has a copy
CERTIFIED
Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 1.5 | -0.51
2 | 2 | -0.31
3 | 2.5 | -0.36
4 | 2.9 | 1
5 | 3.6 | 2.59
6 | 4 | 4
7 | 4.5 | 6.21
8 | 5 | 8.99
9 | 5.5 | 12.58
10 | 6 | 17.29
11 | 6.5 | 21.23
12 | 7 | 26.03
13 | 7.5 | 31.5
14 | 7.9 | 36.53
15 | 8.5 | 43.38
16 | 9 | 48.44
17 | 9.5 | 52.69
18 | 10 | 55.67
19 | 10.5 | 59.17
20 | 11 | 61.24
21 | 11.5 | 61.63
22 | 12 | 61.95
23 | 12.4 | 63.24
24 | 13 | 65.6
25 | 13.4 | 65
26 | 14.1 | 64.28
27 | 14.5 | 64.8

## Bestwind 30
Source: | SWCC Summary Report
As of February 2020 http://smallwindcertification.org/certified-turbines/bestwind-30
PNNL has a copy
CERTIFIED
Bin Number | Hub Height Wind Speed (m/s) | Power Output (kW)
1 | 1.52 | -0.263
2 | 2 | -0.385
3 | 2.56 | -0.541
4 | 3.02 | -0.327
5 | 3.53 | 0.113
6 | 4 | 0.732
7 | 4.5 | 1.56
8 | 4.99 | 2.2821
9 | 5.51 | 4.441
10 | 6 | 5.976
11 | 6.5 | 7.88
12 | 6.99 | 10.19
13 | 7.49 | 12.39
14 | 8.01 | 14.84
15 | 8.5 | 17.64
16 | 9.1 | 19.96
17 | 9.5 | 22.36
18 | 10 | 24.24
19 | 10.49 | 26.1
20 | 10.99 | 27.21
21 | 11.49 | 28.77
22 | 12 | 29.62
23 | 12.48 | 30.36
24 | 12.96 | 31.04
25 | 13.51 | 31.9
26 | 13.97 | 31.99
27 | 14.5 | 32.88
28 | 14.99 | 33.14
29 | 15.51 | 33.93
30 | 15.99 | 34.23
31 | 16.47 | 34.15
32 | 16.95 | 33.9
33 | 17.51 | 34.11
34 | 17.96 | 33.53
35 | 18.54 | 32.67
36 | 18.96 | 32.92
37 | 19.4 | 31.72